## Slide 1
Occupational Specialism: Gas Engineering
K1.16 Scientific principles and concepts as applied to gas engineering
PowerPoint 1.16d: Air, oxygen and ventilation

## Slide 2: Starter
A customer reports:
“Our boiler is in a cupboard. It works fine when the door is open, but it keeps locking out when the door is shut.”
Discuss in pairs:
What could be causing this issue?
What role might air be playing?
What else might you check?

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe the role of oxygen in combustion.
Identify different air types in appliances.
Calculate ventilation requirements.
Explain the risks of inadequate air supply.

## Slide 4: The role of oxygen in combustion
Combustion is a chemical reaction between a fuel and an oxidiser, and in domestic gas systems, that oxidiser is oxygen, drawn from the surrounding air.
Basic combustion reaction:
Methane (CH₄) + Oxygen (O₂) → Carbon Dioxide (CO₂) + Water (H₂O)
This is known as complete combustion – it releases maximum energy and minimal pollutants.

## Slide 5: The role of oxygen in combustion
But what if there's not enough oxygen?
When oxygen levels fall, we get incomplete combustion:
Carbon monoxide (CO) is produced – a deadly, odourless gas.
Soot (carbon particles) forms, leading to blocked heat exchangers and sooting.
Yellow, lazy flame appears – unstable and inefficient.
Energy output drops, and safety risks rise.

## Slide 6: The role of oxygen in combustion
Why air supply matters:
Air contains about 21% oxygen – every gas flame depends on this.
Appliances need a consistent air supply to maintain combustion.
Air also helps to cool the combustion chamber and prevent overheating.
Modern appliances may lock out if airflow is restricted to prevent unsafe burning.

## Slide 7: Types of air in combustion – primary air
The air mixed with the gas before it reaches the burner.
Helps form the air/gas mixture that ignites.
Affects flame shape, temperature, and colour.
Common in injector-type burners (e.g. cookers).
Too little = yellow flame | Too much = lifting flame

## Slide 8: Types of air in combustion – secondary air
The air that mixes with the flame after ignition.
Completes combustion and helps reduce CO.
Found in many open-flue or radiant appliances.
Think of it as “topping up” the oxygen after the flame starts.

## Slide 9: Types of air in combustion – tertiary air
Additional air is introduced even later in the combustion zone.
Often used in high-efficiency appliances or special burners.
Aims to maximise complete combustion and heat extraction.
Helps meet strict emission standards in commercial systems.

## Slide 10: Appliance categories and air requirements
Gas appliances are classified by how they take in air and discharge combustion products.
This affects installation design, flueing, and ventilation needs.

## Slide 11: Appliance categories and air requirements
Type A appliances – No flue, No ventilation connection
Example: flueless heaters, some catering equipment.
No direct outlet for combustion products.
Rely fully on room air for combustion.
Require high levels of ventilation.
Strict limits on where they can be installed (e.g. room volume).
Risk of CO buildup if not ventilated correctly.

## Slide 12: Appliance categories and air requirements
Type B appliances – Open-flued (natural draught)
Example: open-flue boilers, gas fires.
Draw combustion air from the room.
Products of combustion exit via a natural draught flue.
The room must have sufficient permanent ventilation.
Flue performance is affected by air pressure, temperature, and wind.
Combustion air + flue pull both rely on the surrounding air.

## Slide 13: Appliance categories and air requirements
Type C appliances – Room-sealed, balanced flue
Example: modern condensing boilers.
Air drawn from outside via a twin flue or coaxial system.
The combustion circuit is sealed from the room.
Little or no room ventilation required.
Often chosen for safety and energy efficiency.
Ideal for airtight homes or small compartments.

## Slide 14: Appliance categories and air requirements
Always consult manufacturer instructions + Building Regs (Part J).
Ventilation provision must never be compromised.
Category | Air source | Flue type | Ventilation needs
A | Room | None | High – permanent vents
B | Room | Open (natural) | Moderate – depends on appliance rating
C | Outside (via flue) | Room-sealed | Low / minimal

## Slide 15: Calculating ventilation requirements
For open flued appliances with a net input greater than 7 kW:
Required ventilation = (Net Input – 7) × 5 cm²
For a 22 kW open-flued boiler in a kitchen:
(22 – 7) × 5 = 75 cm² of permanent ventilation is necessary.
The vent can be installed anywhere in the room.
If the input is less than 7 kW, no extra ventilation is needed.
Refer to BS 5440-2 for guidance.

## Slide 16: Calculating ventilation requirements
Where air is drawn from the room into a compartment:
Where air is taken directly from outside:
Net Input (kW) | Low-Level Vent (to room) | High-Level Vent (to room)
≤ 70 kW | 20 cm² per kW | Half of low-level
Net Input (kW) | Low-Level Vent | High-Level Vent
≤ 70 kW | 10 cm² per kW | Half of low-level

## Slide 17: Calculating ventilation requirements
Example: 22 kW boiler vented to outside:
Low = 22 × 10 = 220 cm²
High = 220 ÷ 2 = 110 cm²

## Slide 18: Calculating ventilation requirements
A 24 kW open-flued boiler is installed inside a cupboard, drawing air from the room. What ventilation is needed for:
The room
The compartment

## Slide 19: Calculating ventilation requirements
A 24 kW open-flued boiler is installed inside a cupboard, drawing air from the room. What ventilation is needed for:
The room
The compartment
Answer
Room = (24 – 7) × 5 = 85 cm²
Compartment =
  Low: 24 × 20 = 480 cm² High: 480 ÷ 2 = 240 cm²

## Slide 20: Inadequate ventilation – what can go wrong?
1. Incomplete combustion
Not enough oxygen = carbon monoxide (CO) produced.
Yellow/lazy flames.
Formation of soot → blockages and heat damage.
🔥 Silent killer: CO is colourless, odourless, and deadly.
​

## Slide 21: Inadequate ventilation – what can go wrong?
2. Flue failure
Poor draught causes spillage of combustion products.
Products of combustion may leak into the room.
Linked to fatalities when combined with faulty flues or blocked chimneys.
Especially dangerous in air-tight homes or sealed cupboards.
​

## Slide 22: Inadequate ventilation – what can go wrong?
3. Overheating and appliance damage
Cooling air helps prevent component stress.
Insufficient air can shorten appliance lifespan.
Boiler may enter fault lockout due to overheating.
​

## Slide 23: Inadequate ventilation – what can go wrong?
4. Unsafe situations
Classified as:
  AR (At Risk) – if ventilation is inadequate but no immediate danger.
  ID (Immediately Dangerous) – if combustion products are spilling
Action: Isolate the appliance, label, notify the responsible person.
​

## Slide 24: Inadequate ventilation – what can go wrong?
What signs might you see or smell that hint at poor ventilation?
What should you do if you find a cupboard-sealed boiler with no vents?​

## Slide 25: Mechanical vs natural ventilation
Natural ventilation
Achieved via fixed grilles, air bricks, openable windows.
Relies on pressure and temperature differences (stack effect).
Common in domestic settings (kitchens, cupboards, boiler rooms).
No power supply required.
Must be permanently open and free from blockage.

## Slide 26: Mechanical vs natural ventilation
Natural ventilation
Limitations:
Dependent on external conditions (wind/temp).
Can be obstructed by insulation or refurbishment.
Less control over airflow rate.

## Slide 27: Mechanical vs natural ventilation
Mechanical ventilation
Uses powered fans, ductwork and extract systems.
Common in commercial kitchens, plant rooms, and sealed buildings.
Can be interlocked with an appliance (won’t run unless the fan is operational).
Allows precise control of airflow rate.
Must be installed, tested and maintained by a competent person.

## Slide 28: Mechanical vs natural ventilation
Mechanical ventilation
Risks if failed:
Negative pressure = flue spillage
ID/AR classification possible if interlock fails

## Slide 29: Cooling air and combustion air
Cooling air refers to the air utilised to avoid overheating of appliance components.
Commonly present in:
Fan flues
Gas fires
Gas water heaters
It is important to distinguish it from combustion air, although both are vital.

## Slide 30: Design considerations
Designing safe and compliant ventilation isn't just about picking a grille size.
It requires careful assessment of the whole environment, including appliance type, installation location, and air movement.

## Slide 31: Design considerations
1. Room size and volume
Determines available oxygen and natural air replacement
Larger rooms may dilute combustion products more easily
Small or tightly sealed rooms (e.g., utility cupboards, modern airtight homes) need additional venting
Building Regs Part J considers room volume critical for flueless or open-flued appliances

## Slide 32: Design considerations
2. Number and type of appliances
Each appliance has its own heat input and air requirement.
Multiple appliances (e.g. twin boilers) must be considered collectively.
Ventilation sizing is based on the combined kW net input.
Open flue and flueless types need more air than room-sealed (Type C) units.

## Slide 33: Design considerations
3. Installation location
Cupboards and lofts often lack natural air movement.
Confined spaces require dedicated compartment ventilation.
Lofts may need additional high-level vents to counteract temperature differences.
Vent openings must never be blocked by insulation, stored items or boxing.

## Slide 34: Design considerations
4. Ventilation pathways
Must assess proximity to external air:
  Are there external walls suitable for air bricks?
  Can air move freely to and from the appliance?
  Will nearby mechanical extract fans disrupt airflow (e.g. kitchen fans or bathroom extracts)?
  Extractor fans can create negative pressure → flue reversal

## Slide 35: Design considerations
5. Compliance with Regulations and MI
Part J of Building Regulations sets out legal ventilation requirements
Engineers must check:
Appliance installation manual (MI).
Approved Document J (especially for solid fuel and open-flued appliances).
IGEM/G/11 guidance on classifying unsafe ventilation.
Failure to follow MIs may result in unsafe classification or invalidate warranties.

## Slide 36: Knowledge check
What percentage of air is oxygen?
What is the function of primary air?
How many cm² of ventilation are needed for a 10kW open flued appliance?
Why are balanced flue appliances safer in confined spaces?

## Slide 37: Summary
You should now be able to:
Describe the role of oxygen in combustion.
Identify different air types in appliances.
Calculate ventilation requirements.
Explain the risks of inadequate air supply.

## Slide 38
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.