## Slide 1
Occupational Specialism: Gas Engineering
K1.16 Scientific principles and concepts as applied to gas engineering
PowerPoint 1.16e: Flueing and draught principles

## Slide 2: Starter
A customer says: ‘The boiler keeps locking out and there’s condensation on the kitchen window when it runs.’
What might be going on?
What does ‘locking out’ mean for a gas boiler?
Why might condensation appear when the boiler runs?
Could these two symptoms be linked?
What further questions would you ask the customer?

## Slide 3: Objectives
By the end of this session, you should be able to:
Define draught and flueing in the context of gas appliances.
Differentiate between natural, induced and balanced flue systems.
Describe the function and importance of flueing for safe operation.
Interpret results from flue flow and spillage tests.

## Slide 4: What is draught?
Draught is the pressure difference that causes combustion gases to move through an appliance's flue system and safely out into the atmosphere.
It’s the driving force behind flue gas movement — without it, dangerous products like carbon monoxide (CO) and water vapour would build up inside the building.

## Slide 5: What is draught? – key points
Feature | Description
Purpose | To remove combustion products: CO₂, CO, H₂O vapour, excess heat.
How it works | Gases move from high pressure (appliance) to low pressure (atmosphere).
Forms of draught | Natural (from hot gases rising), Mechanical (fan-assisted systems).
What it depends on | Flue temperature, Air pressure, Appliance design, Ventilation.

## Slide 6: What is draught? – scientific principle
Draught = flow of gases caused by a pressure difference.
Hot combustion gases are lighter than cold air, so they rise naturally. This creates an upward flow — a natural draught — which pulls fresh air in and pushes waste gases out.

## Slide 7: What is draught? – real world example
Imagine a room-sealed boiler with no draught due to a blocked flue. The result?
Boiler lockout
Dangerous fume build-up
Condensation or even soot deposits
CO risk to occupants.
This is why testing flue performance is critical during service and commissioning!

## Slide 8: Why flueing matters
Flueing is not optional — it’s a life-saving function built into every gas appliance system.
Without proper flueing, combustion becomes dangerous, inefficient, and illegal.

## Slide 9: Why flueing matters – key functions
Function | What it does
Removes combustion products | Safely vents harmful gases: CO₂, CO, NOx, H₂O vapour, unburnt hydrocarbons.
Supports complete combustion | Maintains correct air supply and draught for a stable flame.
Manages condensation | Prevents moisture build-up in the flue and appliance (esp. condensing boilers).
Protects building fabric | Stops hot gases escaping into lofts or cavities, reducing fire/damage risk.
Maintains appliance efficiency | Ensures proper flame characteristics and energy transfer.
Reduces carbon monoxide (CO) risk | Ensures waste gases leave the building fully and safely.

## Slide 10: Why flueing matters – when flueing fails
Problem | Result
Blocked or leaking flue | Gases leak into occupied rooms → CO poisoning risk.
Inadequate draught | Incomplete combustion → yellow flame, soot, high CO.
Flue not to regulation | Building Regs breach → fails inspection, voids insurance.
Poorly installed flue | Flame instability → safety lockout or overheating.

## Slide 11: Why flueing matters – legal requirements
Gas Safety (Installation and Use) Regulations 1998 (GSIUR)
Regulation 27: appliances must be installed to operate safely.
Regulation 26(9): engineer must check for safety after work.
Regulation 2: “unsafe” includes poor or ineffective flueing.
Building Regulations Approved Document Part J (Combustion Appliances)
Section J2: requires effective discharge of products of combustion.
Appendix C: sets out flue sizing and ventilation examples.
Covers open-flued, room-sealed, and condensing systems.

## Slide 12: Why flueing must be right
Safeguards individuals from harmful gases.
Guarantees that appliances use fuel efficiently.
Avoids issues with legal compliance.
Shields property from potential structural damage and fire hazards.
Essential component of the commissioning and maintenance process.

## Slide 13: Types of draught
Type | Description | Example appliance
Natural Draught | Relies on warm air rising via chimney | Open flue boilers/fires
Induced Draught | Uses a fan to assist flue flow | Fan flue appliances (pre-2000)
Forced Draught | Pressurised airflow into burner or chamber | Commercial plant rooms
Balanced Flue | Sealed system, air in/out via concentric flue | Room-sealed condensing boilers

## Slide 14: Natural draught (passive / buoyancy-driven)
How it works:
Relies on the natural tendency of hot gases to rise due to being less dense than cooler surrounding air.
Where it’s used:
Open-flued appliances
Older heat-only boilers, decorative gas fires
Chimneys and vertical flues without fans.

## Slide 15: Natural draught (passive / buoyancy-driven)
Affected by:
Outdoor temperature (greater temperature difference = stronger draught).
Flue height (taller flue = stronger draught).
Wind pressure and building air tightness.

## Slide 16: Natural draught (passive / buoyancy-driven)
Advantages:
Simple, no mechanical parts
Quiet operation.
Disadvantages:
Susceptible to backdraughts
Ineffective in airtight or poorly ventilated rooms
Performance changes with weather.

## Slide 17: Induced draught
How it works:
A fan is placed at the outlet of the flue to pull combustion gases through the appliance.
Where it’s used:
Industrial burners
Some older mechanical systems
High-rise or commercial buildings.

## Slide 18: Induced draught
Key features:
Fan draws gases out → creates negative pressure.
Improves control over combustion and efficiency.
Reduces risk of flue gas spillage.
Risk if the fan fails:
May cause flue blockage alarms, boiler lockout, or gas buildup inside the appliance.

## Slide 19: Forced draught
How it works:
A fan is located at the inlet, pushing combustion air into the appliance (pre-mixed or air-only).
Where it’s used:
Modern condensing boilers.
Room-sealed appliances.
Commercial appliances with high burner pressures.

## Slide 20: Forced draught
Benefits:
Consistent combustion regardless of external conditions.
More efficient flame control.
Compact flue design possible (horizontal or concentric).
Industry link:
Part of room-sealed systems — air drawn in and gases expelled via a balanced flue, complying with Part J and GSIUR.

## Slide 21: Balanced draught
How it works:
Combination of forced air in and induced exhaust out, often using two fans or a pressure-balanced system.
Where it’s used:
Large commercial and industrial boilers.
Where tight combustion control is critical.

## Slide 22: Balanced draught
Advantages:
Precise control of combustion
Stable flame conditions
High efficiency and safety.
Requires:
Accurate control system
Regular servicing of both fans
Tight air pressure monitoring.

## Slide 23: Chimney and flue systems
Gas appliances must have safe and effective methods for removing combustion products from the property.
These systems are categorised into Type A, B, and C appliances, each with different flue or ventilation needs.

## Slide 24: Chimney and flue systems – Type A
Type A – Flueless appliances
No flue or chimney – combustion products released into the room.
Strict room volume and permanent ventilation requirements.
Not suitable for bedrooms or bathrooms.
Must have flame supervision device (FSD).
High risk if ventilation is blocked or undersized.

## Slide 25: Chimney and flue systems – Type B
Type B – Open-flued appliances
Draw air from the room and discharge gases via chimney or flue.
Relies on natural draught – vulnerable to backdraughts.
Needs permanent ventilation into the room.
Spillage tests are required during commissioning.
Example: Decorative gas fire with open chimney.

## Slide 26: Chimney and flue systems – Type C
Type C – Room-sealed appliances
Draw combustion air from outside and expel gases externally.
Usually a concentric flue (air in/out via same terminal unit).
Much safer – no air exchange with room.
Includes fanned flue boilers, combi boilers, condensing units.
Ideal for modern airtight homes.

## Slide 27: Chimney and flue requirements (Building Regs Part J)
1. Minimum flue height
At least 600 mm above the roof ridge or flat roof.
Prevents recirculation of flue gases into windows or vents.

## Slide 28: Chimney and flue requirements (Building Regs Part J)
2. Safe termination
Must comply with minimum distances from windows, doors, eaves.
Avoids fume re-entry and supports proper dispersal.

## Slide 29: Chimney and flue requirements (Building Regs Part J)
3. Flue lining
Corrosion-resistant liners are required for long-term use.
Must be compatible with the fuel type and appliance.

## Slide 30: Chimney and flue requirements (Building Regs Part J)
4. Inspection access
Flue systems must allow visual inspection and maintenance access.
Especially critical in concealed voids or boxed-in systems.

## Slide 31: Chimney and flue requirements (Building Regs Part J)
5. Manufacturer’s Instructions (MI)
Always override general rules where stated.
Must be followed for installation, flue sizing, and clearances.

## Slide 32: Chimney and flue requirements (Building Regs Part J)
GSIUR 1998 & Part J of Building Regulations require all of the above to ensure:
Safe discharge of combustion gases
Structural protection of buildings
CO risk mitigation.

## Slide 33: Combustion products and condensation
When fuel burns in a gas appliance, it produces combustion products — these must be safely removed to avoid condensation, corrosion, and carbon monoxide (CO) danger.​

## Slide 34: Combustion products and condensation
What are combustion products?
When methane (CH₄) or propane (C₃H₈) burns with oxygen, it produces:
Product | Description
Carbon Dioxide (CO₂) | Harmless gas — a sign of complete combustion.
Water Vapour (H₂O) | Steam — condenses if not removed properly.
Heat (Energy) | Used to heat air/water in the system.
Carbon Monoxide (CO) | Dangerous — from incomplete combustion.
Nitrogen Oxides (NOx) | Environmental pollutant in high-temp systems.

## Slide 35: Combustion products and condensation
Condensation: why it happens
When hot flue gases cool too quickly (below the dew point, around 55°C), the water vapour condenses into liquid on cooler surfaces.
Some causes of condensation in flues are:
Poor flue design or inadequate insulation.
Short flue length or cold external walls.
Oversized flue (reduces gas velocity).
Incorrect flue material (not corrosion-resistant).

## Slide 36: Combustion products and condensation
Dangerous outcomes:
CO Spillage into occupied rooms
Condensate corrosion of heat exchangers and flues
System failure or lockout due to fan/flue sensors
Non-compliance with GSIUR and Part J of Building Regulations.

## Slide 37: Combustion products and condensation
Link to modern technology: condensing boilers
Condensing boilers are designed to encourage condensation of flue gases to reclaim latent heat.
Efficiency is increased.
Flue must be sloped correctly to drain condensate (as per MI and Part J).
Condensing Boiler Feature | Function
Extra-large heat exchanger | Captures heat from water vapour before discharge.
Drain for condensate | Safely removes acidic water to waste pipe.
Plastic (PP) flue materials | Resistant to acidic condensate.

## Slide 38: Combustion products and condensation
Science link: dew point
Dew point is the temperature at which air becomes saturated, and water vapour condenses.
In flue systems:
If flue walls fall below this temp → condensation forms.
Especially common in cold lofts or outside walls.

## Slide 39: Flue flow test
The flue flow test is a critical check to verify that a chimney or flue system is safely and effectively removing combustion products.
This test is typically carried out during commissioning, servicing, or following alterations to the flue or appliance.

## Slide 40: Flue flow test
A flue flow test confirms that the chimney or flue creates a sufficient draught to safely carry combustion gases (CO₂, CO, water vapour, heat) up and out into the atmosphere.
This test is mandatory for open-flued appliances and should be performed before lighting the appliance during installation or reactivation.

## Slide 41: Flue flow test - test method (simplified procedure)
1. Pre-Check:
Inspect the flue throughout its entire length.
Confirm the flue is installed correctly to British Standards.
Ensure chimney is clear of obstructions.
Confirm appliance is not lit.
Check air vents are open and the room is not too airtight.

## Slide 42: Flue flow test - test method (simplified procedure)
2. Warm the flue:
Use a lit match, paper twist, or blowtorch flame.
Hold in the flue opening to preheat and start the draught.
This mimics normal operating conditions.

## Slide 43: Flue flow test - test method (simplified procedure)
3. Introduce smoke:
Place a smoke pellet at the appliance flue connection.
Smoke pellet should produce 5m3 of smoke in a 30 second burn time.
Light it and observe the flow of smoke.
It should rise steadily through the flue and exit at terminal.

## Slide 44: Flue flow test - test method (simplified procedure)
4. Observation (at terminal or roof):
Should see smoke exiting clearly from the terminal.
Smoke should only be emitted from the correct terminal in chimney stacks with multiple flues.
Must not spill back into the room.

## Slide 45: Flue flow test - test method (simplified procedure)
Interpreting the results:
Observation | Meaning
Strong upward flow | Flue is functioning correctly.
Delayed exit | Flue may be partially blocked or cold.
Smoke spillage | Dangerous — poor draught or blockage.
No movement | Immediate risk — ID classification likely.

## Slide 46: Flue flow test - test method (simplified procedure)
Links to Regulations
GSIUR Reg 26(9): Engineer must ensure appliance operates safely after installation.
Part J, Building Regs: Flues must discharge combustion gases effectively.
IGEM/G/11: Defines unsafe situations for spillage and backdraughts.

## Slide 47: Spillage test
A spillage test checks whether combustion gases are escaping (spilling) from an open-flued gas appliance into the room, instead of being drawn safely up the flue.
It is legally required when commissioning, servicing, or inspecting open-flued appliances. Failure to pass this test is classed as Immediately Dangerous (ID) under Gas Industry Unsafe Situations Procedure (GIUSP).

## Slide 48: Spillage test
Why is the test important?
Prevents carbon monoxide (CO) entering the living space.
Ensures the draught is sufficient to carry away combustion gases.
Detects flue faults, blockages, or ventilation issues.
Validates that the appliance operates safely in real conditions.

## Slide 49: Spillage test
When should a spillage test be done?
On commissioning an open-flued appliance.
During routine service/maintenance.
After flue alterations or property changes (e.g. extractor fans).
When investigating CO alarms or poor combustion signs.

## Slide 50: Step-by-step: how to perform a spillage test
Set up the appliance:
Turn off all extract fans and mechanical ventilation.
Close all external doors and windows.
Appliance off and cool (flue not preheated).

## Slide 51: Step-by-step: how to perform a spillage test
Light the appliance:
Allow to run at maximum rate for 5 minutes.
Stabilises combustion and flue conditions.

## Slide 52: Step-by-step: how to perform a spillage test
Apply smoke source:
Hold a smoke match at:
  Draught diverter
  Case seal
  Around burner tray or canopy.

## Slide 53: Step-by-step: how to perform a spillage test
Observe for spillage:
Smoke should be drawn into the appliance and up the flue.
No smoke should drift into the room.
When carrying out a spillage test with an extract fan in an adjacent room, you must repeat the test with the fan operating and all internal doors open, while keeping all windows, external doors, and adjustable vents closed. This ensures the test reflects worst-case ventilation conditions.

## Slide 54: Step-by-step: how to perform a spillage test
Signs of spillage
Symptom | Risk
Smoke escaping into the room. | CO hazard, flue not drawing.
Condensation on mirror/CO detector. | Incomplete combustion or flue fault.
Flame distortion or instability. | Possible air starvation.
Sooting or yellow flame. | Poor combustion, increased CO.

## Slide 55: What if spillage is detected?
Regulation & Compliance
GSIUR 1998 – Regulation 26(9): Gas work must not leave an appliance in an unsafe condition.
IGEM/G/11 – Unsafe Situations:
If a gas appliance fails a spillage test, it must be classified as Immediately Dangerous (ID) and taken out of service immediately. The gas supply to the appliance must be isolated and capped off until the fault is rectified by a competent person.

## Slide 56: Signs of poor flue operation
A flue that is blocked, damaged, incorrectly installed, or not functioning properly can lead to unsafe conditions.
Recognising the warning signs early is vital to prevent injury, appliance damage, or fatal carbon monoxide exposure.

## Slide 57: Signs of poor flue operation – what to look for
Observation | What It suggests
Yellow/brown staining or soot | Combustion products escaping or flue leakage.
Condensation in appliance/room | Inadequate draught or condensing flue gases inside property.
CO alarm activation | Possible flue failure, appliance spillage, or incomplete combustion.
Flame roll-out from burner | Major flue blockage or negative pressure in room.
Boiler fault codes (flue/ignition) | Appliance self-diagnosing unsafe operation.
Excessive condensate discharge | Cold or sloped flue, improper drainage in condensing systems.

## Slide 58: Signs of poor flue operation – whats going wrong?
These issues often indicate:
Backdraughting (gases drawn back into the room).
Blocked flue (birds’ nests, collapsed liner, debris).
Improper termination (too low or too close to window/vents).
Missing/insufficient ventilation.
Negative room pressure (especially with extractor fans running).

## Slide 59: Signs of poor flue operation
Required gas safe actions
Engineers must follow a structured approach:
Investigate
  Check appliance operation, flue route, visual condition.
  Test ventilation, check for spillage, use CO analyser.
Test
  Perform flue flow and spillage tests.
  Use combustion analyser to check for CO/CO₂ ratios.

## Slide 60: Signs of poor flue operation
Required gas safe actions
Notify
  Inform the customer immediately of the unsafe condition
  Issue warning notice and label the appliance.
Classify (per IGEM/G/11 and GIUSP)
  AR (At Risk): Appliance is safe now but could become dangerous
  ID (Immediately Dangerous): Appliance must be shut off now.

## Slide 61: Balanced flue advantages
Air intake and exhaust through a concentric pipe
This airtight system is particularly suited for sealed residences.
Benefits include:
Lower risk of carbon monoxide.
Decreased chance of spillage.
Reduced requirement for internal ventilation.
Commonly found in contemporary room-sealed appliances.
​

## Slide 62: Knowledge check
What is the purpose of draught in a gas appliance?
What is the difference between a balanced and open flue?
What does a flue flow test check?
Name three signs of poor flue performance.

## Slide 63: Summary
You should now be able to:
Define draught and flueing in the context of gas appliances.
Differentiate between natural, induced and balanced flue systems.
Describe the function and importance of flueing for safe operation.
Interpret results from flue flow and spillage tests.

## Slide 64
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.