## Slide 1
Occupational Specialism: Gas Engineering
K1.16 Scientific principles and concepts as applied to gas engineering
PowerPoint 1.16f: Applied science in gas systems

## Slide 2: Starter
A boiler expands when hot. A gas cylinder’s pressure rises as it heats up.
Why do these happen?
Think about:
What happens to gas molecules when heated?
How does this affect pressure, volume, and flow in a sealed vs open system?
Can they link this to anything they’ve seen in real gas installations?

## Slide 3: Objectives
By the end of the session, you should be able to:
State the gas laws relevant to appliance and pipework behaviour.
Apply scientific principles to real-world gas system scenarios.
Interpret data relating to pressure, volume and temperature.
Explain the impact of flow, expansion and compression in gas engineering.

## Slide 4: Key scientific concepts for gas systems
Temperature influences the volume and pressure of gases.
Pressure impacts the flow rate and the efficiency of delivery.
Volume varies depending on temperature and the dimensions of the pipe.
These factors are regulated by fundamental physical principles:
Boyle’s Law
Charles’s Law
Pressure laws
Principles of flow rate ​

## Slide 5: Boyle’s Law (pressure & volume)
“As pressure increases, volume decreases — if temperature remains constant.”
Boyle’s Law shows how gases are compressible: squeeze a gas (increase pressure), and it takes up less space (volume decreases).
Let it expand, and pressure drops.
P1​×V1 ​= P2​×V2​
P1(Initial pressure) x V1(Initial volume) = P2(New pressure) x V2(New Volume)
This equation applies only when the gas temperature is kept constant.

## Slide 6: Boyle’s Law (pressure & volume)
Example calculation
A gas is stored at 100 kPa in a volume of 2 m³. If the pressure increases to 200 kPa, what is the new volume?
The volume halves when the pressure doubles.

## Slide 7: Boyle’s Law (pressure & volume) - application
Application | Boyle's Law effect
Gas cylinders | Pressure increases if space decreases or gas is compressed.
Gas boosters | Compressing gas raises pressure, reducing volume.
Expansion vessels (sealed systems) | Volume of air cushion changes with system pressure.
Pressure drop in pipework | Larger pipe = more volume = lower pressure loss.
Pump priming or purging | Changing pressure alters how much air occupies a space.

## Slide 8: Charles’s Law (temperature & volume)
“As the temperature of a gas increases, its volume increases — if pressure is kept constant.”
In other words: heat up a gas, it expands. Cool it down, it contracts — as long as the container allows the volume to change.
𝑉1 = Initial volume / 𝑇1 = Initial temperature (in Kelvin).
𝑉2​ = Final volume / 𝑇2​ = Final temperature (in Kelvin).
Temperatures must be converted to Kelvin (K). K = °C + 273.

## Slide 9: Charles’s Law (temperature & volume)
A gas occupies 2.0 m³ at 20°C. What volume will it occupy at 80°C, if pressure remains constant?
Convert to Kelvin:
T1=20+273=293K
T2=80+273=353K
The gas expands as it heats up.

## Slide 10: Charles’s Law (temperature & volume)
Application | Charles’s Law in action
LPG cylinders in hot weather | Liquid expands, increasing internal gas pressure.
Gas meters | Internal volume of air/gas varies slightly with temperature.
Expansion tanks | Air/gas inside expands when heated, maintaining system pressure.
Boiler casings | Air inside expands, increasing internal pressure.
Plastic pipework & seals | Hot gases expand pipe walls, possibly loosening connections.

## Slide 11: Pressure-Temperature Law
“As the temperature of a gas increases, its pressure increases — if the volume stays constant.”
In a sealed system (e.g. gas cylinder, boiler casing), heating the gas causes pressure to rise. Cooling it down causes pressure to fall.
P 1 ​ = Initial pressure
T 1​ = Initial temperature (in Kelvin)
P 2​ = Final pressure
T 2​ = Final temperature (in Kelvin)

## Slide 12: Pressure-Temperature Law
A sealed gas vessel is at 200 kPa and 20˚C. What is the pressure if the temperature rises to 80˚C?
Convert to Kelvin:
T1=20+273=293K
T2=80+273=353K
Pressure rises as temperature increases.

## Slide 13: Pressure-Temperature Law - application
Application | Effect of Temperature on Pressure
LPG cylinders in direct sun | Internal pressure increases – can activate relief valve.
Sealed central heating systems | Heated water expands gas inside expansion vessel.
Gas meters in warm spaces | Can give slight pressure variance (temp effect).
Gas pipe testing (pressure drop) | External temperature can cause misleading readings.
Gas storage & safety | Overpressure = risk of explosion if not regulated.

## Slide 14: Flow rate and pipe sizing
Gas must flow at a sufficient rate and pressure to supply appliances safely and efficiently. Pipe size and material directly affect how gas flows through a system.​
Flow Rate = the volume of gas delivered per unit of time.

## Slide 15: Flow rate and pipe sizing
Flow rate is quantified in m³/h or l/min.
Factors influencing it include:
Pressure differential
Diameter and length of the pipe
Quantity of bends and fittings
Type of gas (Natural Gas or Liquefied Petroleum Gas).
​

## Slide 16: Pipe sizing: Worked Example
• Appliance: Condensing gas boiler
• Heat Input: 30 kW
• Location: Kitchen (ground floor)
• Meter Position: External, 12 m away
• Pipe Route: 4 elbows, 1 tee
• Gas Type: Natural gas (G20 methane)
• System Pressure: Low pressure
• Material: Copper pipe
​

## Slide 17: Pipe sizing: Worked Example
Calculate Gas Rate (m³/h)
• Assumes calorific value (CV) of 38.7 MJ/m
​

## Slide 18: Pipe sizing: Worked Example
Determine Equivalent Length
• Straight pipe: 12 m
• Fittings:
• 4 elbows × 0.5 m = 2 m
• 1 tee × 0.5 m = 0.5 m
• Total Equivalent Length = 12 + 2 + 0.5 = 14.5 m
​

## Slide 19: Pipe sizing: Worked Example
Select Pipe Size from Sizing Tables
• Required flow: 2.79 m³/h
• Equivalent length: 14.5 m
• From BS 6891 or manufacturer tables:
• 22 mm copper pipe supports ~18 m at 2.79 m³/h
• 22 mm copper pipe is suitable.
​

## Slide 20: Pipe sizing: Worked Example
Verify Pressure Drop
• Max allowable drop: 1 mbar
• Estimated drop for 22 mm over 14.5 m at 2.79 m³/h ≈ 0.8 mbar
​

## Slide 21: Why is pipe sizing so important?
Factor | Impact
Undersized pipe | Starves appliance of gas → flame instability, poor combustion.
Oversized pipe | More costly and difficult to install.
Too many fittings/bends | Causes resistance → reduces pressure and flow rate.
Incorrect material | Can affect friction and safety (e.g. copper vs MDPE).
Long pipe runs | Require careful sizing to prevent excessive pressure drop.

## Slide 22: Flow rate and pipe sizing
Key Design Rule (for Natural Gas).
Allowable pressure drop:
Max 1 mbar from meter to appliance (as per IGE/UP/2).
Use pipe sizing tables or software to ensure this is not exceeded.

## Slide 23: Flow rate and pipe sizing
Pipe Sizing Formula (Simplified Conceptual):
𝑄 = Flow rate
𝐷 = Internal diameter
Δ𝑃 = Pressure difference
𝐿 = Length of pipe
Small increases in diameter significantly boost flow.

## Slide 24: Flow rate and pipe sizing
Materials and internal roughness.
Use conversion fittings and ensure joints are accessible unless buried and protected.
Pipe material | Typical use | Friction level
Copper | Domestic pipework | Low
Steel | Commercial/industrial | Medium
MDPE (yellow) | Underground external supplies | Very low

## Slide 25: Flow rate and pipe sizing
Real-world engineering application
Scenario | Pipe sizing implication
24 kW combi boiler in upstairs flat | Long vertical run = larger pipe needed to maintain pressure.
Multiple appliances on one line | Total load must be calculated and distributed across branches.
LPG supply from external tank | Higher pressure but lower calorific volume = different sizing rules.
Cooker + boiler on same branch | Sizing must allow for simultaneous use.

## Slide 26: Pressure drop in gas systems
As gas flows through a pipe, it loses pressure due to resistance from the pipe walls, fittings, and changes in direction.
Too much pressure loss can lead to poor appliance performance, flame instability, or even unsafe operation.

## Slide 27: What is pressure drop in gas systems
Pressure drops as gas travels from the meter to the appliance.
Caused by:
  Pipe length
  Diameter (smaller pipe = more resistance)
  Number of bends and fittings
  Flow rate (more flow = more friction).
This pressure drop is expected — but must be kept within safe limits.

## Slide 28: What is pressure drop in gas systems
Maximum permitted pressure drop (Natural Gas):
Standing Pressure - ~ 21 mbar (at meter outlet).
Operating Pressure - Measured while appliance is running.
Allowable Drop (NG) - Max 1 mbar from meter to appliance.
e.g., Standing Pressure = 21 mbar → Operating Pressure must be ≥ 20 mbar.

## Slide 29: How to test for pressure drop
1. Use a U-Gauge or Digital Manometer.
Connect to the meter test point for standing and working pressure.
2. Measure:
Standing pressure – no appliances on
Working pressure – appliance on full rate
Calculate pressure drop
3. Compare with permissible limit
✅ ≤ 1 mbar drop → OK ❌ > 1 mbar drop → investigate

## Slide 30: Energy transfer – heat and work
Combustion = chemical energy → heat.
Heat = energy in transfer due to temperature difference.
Work = force acting through a distance (e.g. gas moving through a pipe).
Units:
Energy = Joules (J)
Power = Watts (W) = Joules/second
Heat input/output = kW
Heat calculation for air: Q = mcΔT (mass × specific heat capacity × temp change).

## Slide 31: Energy transfer – heat and work
In gas systems, energy is transferred as either heat (thermal energy) or work (mechanical energy).
These transfers are essential for heating water, moving gases, or powering components.
What Is Heat?
Heat is the transfer of energy due to a temperature difference.
Always moves from hot ➜ cold.
Caused by vibration and movement of molecules.
In gas systems: generated by combustion.

## Slide 32: Energy transfer – heat and work
What Is Work?
Work is done when energy causes movement or force over a distance.
Often involves pressure pushing gas or moving parts.
In gas engineering: work occurs in fans, pumps, gas expansion, valves.
Work in Action | How It Happens
Fan pushes combustion air. | Mechanical energy drives airflow.
Gas expands in burner. | Pressure causes movement, creating flame spread.
Gas valve opens under pressure. | Work is done to overcome resistance.

## Slide 33: Energy transfer – heat and work
How They Link: First Law of Thermodynamics.
Energy can’t be created or destroyed – only transferred as heat or work.
In a sealed system:
Combustion adds heat energy.
Some heat goes into the system water.
Some energy is used to do work (e.g. move water/gas).
Some is lost to surroundings (inefficiency).

## Slide 34: Energy transfer – heat and work
Key scientific terms
Term | Meaning
Conduction | Heat transfer through solid materials.
Convection | Heat carried by moving fluids/gases.
Radiation | Heat emitted as infrared energy (no contact).
Work | Force applied over a distance.

## Slide 35: Thermal expansion
Thermal expansion refers to the tendency of materials to increase in size when heated and decrease when cooled.
Gas systems experience impacts from repeated heating cycles.
Frequently affected materials include: copper, steel, aluminium, flue pipes, appliance casings, and gas pipes.

## Slide 36: Why thermal expansion matters
When components heat up:
Pipes may lengthen, causing stress at joints.
Flue sections may shift or warp, risking poor combustion gas removal.
Seals may break, allowing carbon monoxide to leak.
High pressure may build in confined pipework, affecting gas flow rates and appliance safety.

## Slide 37: Examples of expansion related hazards
IGEM/G/11 guidance mandates competent engineers identify and act on unsafe expansion risks.
Component | Effect of expansion | Potential risk
Flue pipes | Warping or misalignment | Flue gas spillage or CO leaks
Flexible joints | Stretching or fatigue | Gas leaks
Appliance seals | Hardening/cracking under temperature | Incomplete combustion
Pressurised pipework | Pressure increase | Risk of rupture or appliance shutdown

## Slide 38: Thermal expansion
How engineers manage thermal expansion:
Use of expansion loops or flexible hoses in gas pipework.
Articulated flue sections or telescopic ducts.
High-temperature sealants and gaskets.
Installation of thermal breaks in long metal runs.
Manufacturer's Instructions (MI) must always be followed for spacing and fixings.

## Slide 39: Thermal expansion
Key concept: differential expansion
Different materials expand at different rates:
Steel expands less than copper.
Composite materials may deform if mismatched.
Engineers must account for this in multi-material assemblies to avoid stress fractures or seal failures.

## Slide 40: Applying the science – fault scenarios
1. Boiler pressure rises to 3 bar when hot – why? 2. Cooker flame dims when oven ignites – what’s the cause? 3. A long pipe run loses pressure at the appliance – how do we solve it?
Discuss and justify answers using science from this session.

## Slide 41: Knowledge check
Quick recap quiz:
What happens to gas volume when temperature increases?
State Boyle’s Law in your own words.
Why do we allow for a 1 mbar pressure drop in NG systems?
What factors affect gas flow in pipework?

## Slide 42: Summary
You should now be able to:
State the gas laws relevant to appliance and pipework behaviour.
Apply scientific principles to real-world gas system scenarios.
Interpret data relating to pressure, volume and temperature.
Explain the impact of flow, expansion and compression in gas engineering.

## Slide 43
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.