## Slide 1
Occupational Specialism: Gas Engineering
K1.10 Safety devices applicable to gas systems, their characteristics and operation
PowerPoint 1.10a: ECV, UPSO, OPSO, SSOV and resetting procedures

## Slide 2: Starter
Scenario challenge
Simon is called to a site where no gas is reaching the appliances. The emergency control valve is open, and the meter regulator appears normal.
Discussion points
What other devices might stop gas flow?
Why might they operate without a visible leak?
How would you test them?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify the core gas safety shut-off devices in a gas system.
Explain the function and activation conditions of ECV, UPSO, OPSO, SSOV.
Describe the correct testing and resetting procedures for each.
Understand when replacement or further action is required.

## Slide 4: Emergency Control Valve (ECV)
Function and purpose
The Emergency Control Valve serves as the primary manually operated isolation point for the gas supply. It provides a quick and accessible means to shut off gas flow in emergency situations or during maintenance work.
ECVs are required by the Gas Safety (Installation and Use) Regulations (GSIUR) Regulation 9, which mandates an operable ECV on every gas installation. This regulation ensures that occupants and engineers have a means to isolate the gas supply when necessary.

## Slide 5: Emergency Control Valve (ECV)
Key features
Quarter-turn handle design for quick operation.
Must be clearly marked with "on" and "off" positions.
Must remain accessible at all times.
Located at the inlet to the gas meter (internal or external).
Operated by turning 90° clockwise to close.

## Slide 6: Emergency Control Valve (ECV)
Engineering note
When working on a gas system, always confirm the ECV operates freely. Stiff or damaged ECVs must be reported and replaced. Test by turning off and on smoothly before commencing work.

## Slide 7: Under Pressure Shut-Off Valve (UPSO)
Function and operation
The Under Pressure Shut-Off Valve (UPSO) is a crucial safety device that automatically shuts off gas flow when the inlet pressure drops below a predetermined safe limit.
This prevents potential partial combustion issues that could lead to dangerous carbon monoxide production.

## Slide 8: Under Pressure Shut-Off Valve (UPSO)
UPSOs are designed to detect pressure drops that might be caused by:
Upstream pipe leakage or damage.
Regulator failure or freezing.
Supply interruption from the mains.
Blockages in the filter or pipework.

## Slide 9: Under Pressure Shut-Off Valve (UPSO)
Common applications
UPSOs are frequently found in:
LPG tank and cylinder installations.
Natural gas installations where regulators are prone to blockage.
Commercial kitchens with high gas demand.
Multiple meter installations.

## Slide 10: Under Pressure Shut-Off Valve (UPSO)
Resetting procedure
After a UPSO has activated, it requires a specific reset procedure:
Identify and rectify the cause of low pressure.
Verify that upstream pressure has been restored to normal.
Locate the manual reset button (typically red or yellow).
Press and hold the reset button for the specified time (usually 5-10 seconds).
Release button and check for gas flow restoration.
Perform a tightness test on the downstream installation.

## Slide 11: Under Pressure Shut-Off Valve (UPSO)
Never attempt to reset a UPSO without first determining and resolving the cause of activation.
Forcing a reset could create a dangerous situation if the underlying issue remains.

## Slide 12: Over Pressure Shut-Off Valve (OPSO)
Function
The Over Pressure Shut-Off Valve (OPSO) automatically shuts off gas flow when pressure exceeds the maximum safe operating limit.
This protects downstream pipework, appliances, and components from potential damage or failure due to excessive pressure.

## Slide 13: Over Pressure Shut-Off Valve (OPSO)
High pressure conditions can lead to:
Gas leakage at joints and connections.
Regulator diaphragm damage.
Appliance control valve failure.
Excessive flame size and incomplete combustion.

## Slide 14: Common applications
OPSOs are typically found in:
LPG systems where pressure regulation is critical.
Bulk tank installations.
Metered estates with shared supply systems.
Commercial and industrial gas installations.
They are usually fitted upstream of the meter or main pressure regulator.

## Slide 15: Resetting procedure
After an OPSO activation:
Investigate and resolve the cause of overpressure
Check for damage to downstream components.
Verify pressure has stabilised to normal range.
Follow reset procedure specific to the device
Some OPSOs automatically reset once pressure normalises, while others require manual intervention by a qualified engineer. Always check manufacturer instructions.
All OPSOs must be tested after activation and the cause thoroughly investigated. Repeated activations indicate a systemic issue requiring immediate attention.

## Slide 16: Safety Shut-Off Valve (SSOV)
Function and purpose
The Safety Shut-Off Valve (SSOV) is the final protective device within a gas appliance that prevents gas flow to the burner unless safe combustion conditions are confirmed. It works as the "last line of defence" before gas reaches the burner.

## Slide 17: Safety Shut-Off Valve (SSOV)
SSOVs will automatically shut off gas when:
No flame is detected during or after ignition sequence.
Flame is lost during normal operation.
Combustion parameters fall outside safe limits.
Pressure drops below minimum or exceeds maximum.
Appliance control failure occurs.
Overheating is detected.

## Slide 18: Safety Shut-Off Valve (SSOV)
Control systems
SSOVs are controlled by:
Flame supervision devices (thermocouples, flame rectification).
Printed circuit boards (PCBs) in modern appliances.
Pressure switches monitoring fan operation.
Temperature limiters and thermal cut-outs.

## Slide 19: Safety Shut-Off Valve (SSOV)
Common locations
SSOVs are integrated components within:
Boilers (combination, system, and conventional).
Water heaters (instantaneous and storage).
Gas fires and heaters.
Cookers and commercial catering equipment.
They are typically incorporated into the multifunctional gas valve assembly but can also be separate components in complex systems.

## Slide 20: Safety Shut-Off Valve (SSOV)
Modern developments
Contemporary appliances often incorporate multiple safety systems working together, including:
Dual SSOVs for redundant protection.
Microprocessor-controlled ignition sequencing.
Self-diagnostic capabilities with fault code display.
Remote monitoring via internet connection.

## Slide 21: Testing and resetting procedures
Device | Test method | Reset method | Key considerations
Emergency Control Valve (ECV) | Visual inspection, check for free movement, verify clear on/off markings. | N/A – manually operated handle. | Must be accessible and operable by all occupants. Check for corrosion or stiffness. Lubrication is not permitted.
Under Pressure Shut-Off Valve (UPSO) | Simulate low pressure condition, observe shut-off action (using approved test equipment). | Manual reset button (only after confirming inlet pressure has been restored). | Never reset without identifying and resolving the cause. Multiple activations indicate a systemic issue.
Over Pressure Shut-Off Valve (OPSO) | Simulate high pressure condition using proper test rig only. Never exceed manufacturer's test limits. | Manual reset after pressure check and verification of downstream safety. | Must be tested during commissioning and when activation occurs. Some models require specialised tools.
Safety Shut-Off Valve (SSOV) | Operate appliance, interrupt flame signal or create fault condition according to manufacturer's instructions | Automatic or PCB-controlled reset. Some require manual intervention. | Test procedure varies by appliance type. Always consult specific manufacturer's instructions and record results.

## Slide 22: Knowledge check
Emergency Control Valve (ECV): What is the primary purpose of an Emergency Control Valve, and who should be able to operate it? Explain the regulatory requirement regarding ECVs.
Under Pressure Shut-Off (UPSO): Under what conditions would an UPSO activate? Provide at least three potential causes and explain how you would safely reset the device after resolving the issue.
Complete these questions individually before comparing your answers with colleagues. Be prepared to explain your reasoning.

## Slide 23: Knowledge check
Over Pressure Shut-Off (OPSO): What checks must be performed before resetting an OPSO that has activated? Why is it essential to investigate the cause rather than simply resetting the device?
Safety Shut-Off Valve (SSOV): Explain how an SSOV determines when to shut off gas flow. Describe the different types of flame detection systems commonly used and how they interface with the SSOV.
Complete these questions individually before comparing your answers with colleagues. Be prepared to explain your reasoning.

## Slide 24: Inside a modern boiler: SSOV integration
Multifunctional gas valve assembly
Modern boilers incorporate sophisticated safety systems centred around the SSOV. The multifunctional gas valve assembly typically includes:
Dual solenoid-operated safety shut-off valves in series.
Modulating valve for precise gas flow control.
Pressure regulator to maintain stable gas pressure.
Filter to prevent debris from reaching sensitive components.
Pressure test points for diagnostic measurements.

## Slide 25: Inside a modern boiler: SSOV integration
Safety interlock system
The SSOV operation is controlled by multiple safety circuits:
Flame rectification electrode monitoring presence of flame.
Air pressure switch confirming fan operation.
Temperature sensors detecting overheating.
Flow switches verifying adequate water circulation.
PCB microprocessor coordinating safety sequence.

## Slide 26: Inside a modern boiler: SSOV integration
Failure modes and diagnostics
Common SSOV-related faults include:
Failure to open due to electrical supply issues.
Mechanical sticking from debris or corrosion.
Coil failure preventing electromagnetic operation.
Valve seat damage causing leakage.
Electronic control board communication errors.

## Slide 27: Inside a modern boiler: SSOV integration
Failure modes and diagnostics
When diagnosing SSOV faults:
Check fault codes on appliance display.
Measure voltage to valve coils during ignition sequence.
Test resistance of valve coils (refer to manufacturer specs).
Verify proper flame detection signal.
Check for blockages in gas path.

## Slide 28: Key takeaways
Essential safety device functions
Emergency Control Valve (ECV): Manual isolation point for gas supply, required by GSIUR Reg. 9, must be accessible to all occupants and clearly marked.
Under Pressure Shut-Off (UPSO): Automatic protection against low-pressure conditions that could cause incomplete combustion. Requires manual reset after resolving the cause.

## Slide 29: Key takeaways
Over Pressure Shut-Off (OPSO): Prevents excessive pressure reaching downstream components. Common in LPG systems and commercial installations.
Safety Shut-Off Valve (SSOV): This is the final protection within appliances. It prevents gas flow unless safe combustion is confirmed via flame detection systems.

## Slide 30: Key takeaways
Critical engineering principles
Always investigate the cause of safety device activation before attempting to reset.
Document all tests and interventions in accordance with Gas Safe requirements.
Never bypass or defeat safety devices, even temporarily.
Follow the manufacturer's instructions for testing and reset procedures.
Consider the system holistically - one activated device may indicate problems elsewhere.
Communicate clearly with customers about the purpose and importance of safety devices.

## Slide 31: Summary
You should now be able to:
Identify the core gas safety shut-off devices in a gas system.
Explain the function and activation conditions of ECV, UPSO, OPSO, SSOV.
Describe the correct testing and resetting procedures for each.
Understand when replacement or further action is required.

## Slide 32
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.