## Slide 1
Occupational Specialism: Gas Engineering
K1.10 Safety devices applicable to gas systems, their characteristics and operation
PowerPoint 1.10d: Testing, inspection and replacement procedures

## Slide 2: Starter
Scenario Charlie finds a faulty air pressure switch in a combi boiler. The appliance is out of warranty and parts are no longer available. He considers fitting a ‘universal APS’ he found online.
Prompt questions
Should Charlie install the universal part?
What regulations or guidance apply?
What would be the safer alternative?

## Slide 3: Objectives
By the end of this session, you should be able to:
List the steps for testing key safety devices in gas systems.
Identify when a device is faulty or out of tolerance.
Explain safe procedures for replacing safety-critical components.
Apply compliance checks using MI, GSIUR, and Gas Safe guidelines.

## Slide 4: Regulation 26 (9) Gas Safety (Installation and Use) Regulations 1998
Regulation 26(9) applies to any person who carries out work on a gas appliance. It mandates that immediately after completing the work, the operative must examine and test the appliance to ensure it is safe for continued use. After completing work on a gas appliance, the operative must check:
Effectiveness of any flue – to ensure safe discharge of combustion products.
Supply of combustion air – to confirm adequate ventilation for safe operation.
Operating pressure or heat input – or both, as necessary.

## Slide 5: Regulation 26 (9) Gas Safety (Installation and Use) Regulations 1998
Combustion performance – if it’s not reasonably practicable to measure pressure or heat input, as per paragraph 26(9).
Safe operation of the appliance – to confirm it functions safely under normal conditions.
These checks must be performed immediately after the work is completed.

## Slide 6: Inspection procedures: Visual and functional
Visual inspection elements
Secure mounting – no loose or damaged fixings.
No signs of corrosion, burning or heat damage.
Wiring and terminals intact – no fraying or loose connections.
No blockages in tubing (especially for APS, gas valves).
Correct labelling or approval marking (UKCA/CE).
No modification or tampering with evidence.
Appropriate clearances maintained.
Correct orientation and positioning.

## Slide 7: Inspection procedures: Visual and functional
Functional checks
Must be performed during commissioning and servicing.
Simulate demand/load conditions and check operation.
Verify reset functions work correctly.
Test safety cut-offs activate within parameters.
Check for correct sequencing of operations.
Monitor response times against specifications.
Verify correct operation across the operating range.
Confirm audible/visual alarms function correctly.

## Slide 8: Inspection procedures: Visual and functional
IGEM/G/11 and Gas Safe guidance strongly recommend documented safety checks for all inspections, with evidence retained for at least 6 years.
Remember: Both visual and functional testing must be performed in sequence, with any anomalies recorded and addressed before the appliance is deemed safe for use. All checks should follow manufacturer-specific guidance where available.

## Slide 9: Testing safety devices: methods and fault indicators
Device | Common test methods | Result if faulty | Acceptance criteria
Air Pressure Switch (APS) | Fan on → check continuity across terminals; measure pressure differential | Burner won't ignite / lockout; error code display | Continuity at specified pressure; opens/closes at correct setpoints
Flame Supervision Device (FSD) | Check flame current (μA) or thermocouple mV output; response time test | Gas shuts off / flame dies on release; nuisance lockouts | Thermocouple: 8-30mV; Flame rod: >1μA (typically 3-5μA)
CO Alarm | Press test button; use calibrated test gas if available | No alarm; LED or sound error; no response to test gas | Alarm activates when tested; replace after 5-7 years regardless
Thermostats | Resistance test across range of temperatures; operation test | Boiler over/underheats; short cycling; no cut-off | Consistent resistance readings; activates within ±3°C of setpoint
Low Water Pressure Switch | Pressurise system → check continuity; simulate pressure drop | No ignition; low pressure error; fails to detect low pressure | Activates at manufacturer-specified low pressure (typically 0.5-0.8 bar)
Safety Shut-Off Valve (SSOV) | Operate appliance → observe closure timing; leak test | Gas valve does not shut or open properly; slow response | Closes within safety time (typically <1 second); no leakage
High Limit Thermostat | Simulate overheat condition; resistance check | Fails to cut off at high temperature; reset button failure | Cuts out at specified temperature (typically 80-100°C)

## Slide 10: Safe replacement procedures
Preparation
Isolate gas supply and verify with leak detection fluid.
Disconnect electrical supply and verify with approved voltage tester.
Verify part number against manufacturer instructions (MI).
Source certified part with proper UKCA/CE marking.
Gather appropriate tools and personal protective equipment (PPE).
Inform customer of procedure and estimated completion time.

## Slide 11: Safe replacement procedures
Replacement steps
Isolate and depressurise the system as required.
Label wires before disconnection if applicable.
Remove damaged/faulty component following MI.
Compare the new component with the old to verify compatibility.
Install manufacturer-approved replacement as specified.
Check all seals, connections and wiring.
Ensure correct positioning and orientation.

## Slide 12: Safe replacement procedures
Commissioning and testing
Reconnect electrical supply and gas supply.
Pressure test any gas joints using approved methods.
Perform appropriate functional tests of the new component.
Verify entire appliance operation through complete cycle.
Check for correct combustion using flue gas analyser.
Document all test results and replacement details.
Update service record and Benchmark logbook.

## Slide 13: Safe replacement procedures
Never modify or bypass a safety device under any circumstances!
This is dangerous, illegal, and could result in the revocation of Gas Safe registration.

## Slide 14: Recordkeeping and compliance
Required documentation
Appliance Benchmark logbook: Complete all relevant sections for installation, commissioning and service.
Landlord/Homeowner Gas Safety Certificate (CP12): Update with details of safety device replacements.
Engineer's job notes: Detailed record of work performed, parts replaced, and testing completed.
System test results: Record all test measurements (gas tightness, CO levels, pressure readings, etc.).

## Slide 15: Recordkeeping and compliance
Required documentation
Component labelling: Apply a dated label to appliance, noting replacement parts.
Parts warranty information: Provide to customer and keep a copy.
Risk assessment: Document any specific risks and mitigations.

## Slide 16: Recordkeeping and compliance
All documentation must be:
Clear and legible
Signed and dated
Stored securely (both physical and digital copies)
Retained for minimum 6 years
Accessible for Gas Safe audit purposes
Provided to customer/property owner
Gas Safe Register audits require full traceability of all safety-related work. Insufficient documentation can result in disciplinary action, including removal from the register.

## Slide 17: Case study: Gas fire lockout investigation
A customer reports that their gas fire locks out after approximately 5 minutes of operation.
The previous engineer replaced the thermocouple, but the problem persists.
Upon arrival, you note good gas pressure but detect a small draught near the flue terminal.

## Slide 18: Case study: Gas fire lockout investigation
Task analysis: What's your inspection sequence?
Verify gas tightness and pressure.
Check ventilation requirements are met.
Inspect flue condition and termination.
Test thermocouple output during operation.
Check for draughts affecting flame stability.
Inspect oxygen depletion system (ODS) operation.
Measure CO/CO₂ ratio in combustion products.

## Slide 19: Case study: Gas fire lockout investigation
Safety devices potentially causing the issue
Oxygen Depletion System (ODS): Could be activating due to poor combustion or ventilation issues.
Thermocouple/Thermopile: May be marginally functional but failing under continuous operation.
Spillage monitoring device: May be detecting products of combustion re-entering the room.
Flame supervision device: Could be mis-positioned or damaged.

## Slide 20: Case study: Gas fire lockout investigation
Replacement/repair steps
Confirm draught issue by smoke testing around the flue terminal.
Inspect flue for blockages or damage requiring clearance/repair.
Check ODS pilot assembly for correct positioning and cleanliness.
Test thermocouple/thermopile output under load (in mV).
Replace ODS pilot assembly if tests indicate failure.
Commission appliance and verify operation for a minimum of 20 minutes.
Document all findings and remedial actions.

## Slide 21: Air Pressure Switch (APS) testing procedure
Function and purpose
The Air Pressure Switch (APS) is a critical safety device that ensures proper combustion air flow before allowing gas valve operation.
It prevents operation when:
The fan is not running.
The flue is blocked.
The air intake is restricted.

## Slide 22: Air Pressure Switch (APS) testing procedure
Testing equipment required
Digital manometer with appropriate range (typically 0-25 mbar).
Digital multimeter with continuity function.
Manufacturer's specifications for switch operating points.
Appropriate tubing and connectors.

## Slide 23: Air Pressure Switch (APS) testing procedure
Testing procedure
Isolate electrical supply to the appliance.
Locate the APS and identify positive/negative pressure ports.
Disconnect the hoses, noting their positions.
Set multimeter to continuity/resistance mode.
Connect meter probes to APS terminals.
At rest, switch should be open (no continuity).

## Slide 24: Air Pressure Switch (APS) testing procedure
Testing procedure
Reconnect hoses and electrical supply.
Run appliance and verify switch closes (continuity).
Measure pressure differential across the switch.
Compare to the manufacturer's specifications.
Most modern boilers display a fault code if the APS fails to close during the startup sequence. Depending on the manufacturer, typical fault codes include F1, F2, F3, or E1. Always check the technical manual for specific codes.

## Slide 25: Flame supervision devices: Testing and replacement
Thermocouple testing
Thermocouples generate a small electrical current (millivolts) when heated by the pilot flame.
With pilot lit, disconnect thermocouple at gas valve end.
Connect digital multimeter set to mV DC range.
Reading should be between 8-30mV (check specific MI).
Slow response or low readings indicate replacement needed.
Test "open circuit" voltage and "closed circuit" voltage if possible.
A healthy thermocouple should maintain at least 12mV under load conditions.

## Slide 26: Flame supervision devices: Testing and replacement
Flame rectification testing
Modern appliances often use flame rectification systems instead of thermocouples.
Isolate the electrical supply.
Disconnect the flame-sensing electrode wire.
Connect a microammeter in series (typically μA DC range).
Restore power and start the appliance.
Measure flame current - should exceed 1μA (typically 3-5μA).
Check electrode position relative to flame.
Flame current below 1μA indicates the need for electrode cleaning or replacement.

## Slide 27: Flame supervision devices: Testing and replacement
Safe replacement procedure
When replacement is necessary:
Isolate gas and electrical supplies.
Allow components to cool if recently operated.
For thermocouples: use the correct spanner to avoid damage to threads.
For electrodes: note exact position before removal (take photo).
Install replacement, maintaining the exact positioning.
For thermocouples: hand-tighten plus 1/4 turn only.
For electrodes: maintain specified gap to burner (typically 3-5mm).

## Slide 28: Flame supervision devices: Testing and replacement
Safe replacement procedure
Flame supervision devices require careful handling during replacement.
Overtightening thermocouples can damage internal components, while incorrect electrode positioning can cause nuisance lockouts or unsafe operation.
Always verify proper operation through multiple operating cycles after replacement.

## Slide 29: Flame supervision devices: Testing and replacement
Safe replacement procedure
When replacement is necessary:
Isolate gas and electrical supplies.
Allow components to cool if recently operated.
For thermocouples: use the correct spanner to avoid damage to threads.
For electrodes: note exact position before removal (take photo).
Install replacement, maintaining exact positioning.

## Slide 30: Flame supervision devices: Testing and replacement
For thermocouples: hand-tighten plus 1/4 turn only.
For electrodes: maintain specified gap to burner (typically 3-5mm).
Flame supervision devices require careful handling during replacement. Overtightening thermocouples can damage internal components, while incorrect electrode positioning can cause nuisance lockouts or unsafe operation.
Always verify proper operation through multiple operating cycles after replacement.

## Slide 31: Gas pressure switches and safety controls
Types and functions
Device type | Function | Test method
Low Gas Pressure Switch | Prevents operation if gas supply pressure insufficient | Pressure gauge and continuity test
High Gas Pressure Switch | Shuts down if gas pressure exceeds safe limit | Pressure gauge and continuity test
Gas Proving System | Verifies gas tightness before ignition | Timed pressure drop test
Low Water Pressure Switch | Prevents operation with insufficient water | Pressure gauge and continuity test

## Slide 32: Gas pressure switches and safety controls
These pressure switches are especially critical in commercial and industrial gas applications, where operating outside pressure parameters can create significant hazards.
Most switches are ‘normally open’ or ‘normally closed’, depending on their safety function in the control circuit.

## Slide 33: Gas pressure switches and safety controls
Testing procedure for gas pressure switches
Identify switch type and normal state (NO/NC).
Isolate electrical supply.
Connect a manometer to the appropriate test point.
Connect the multimeter to the switch terminals.
Gradually alter system pressure and note the exact pressure at which the switch changes state.
Compare to manufacturer's specifications (typically ±10% tolerance).
Verify switch returns to the normal state when pressure normalises.
Check for hysteresis (difference between activation and reset pressures).

## Slide 34: Gas pressure switches and safety controls
Pressure switches are precision instruments that are not typically field-adjustable. If operating outside specifications, the entire switch assembly must be replaced with an exact manufacturer-approved equivalent.
Never attempt to modify switch settings unless specifically instructed by the manufacturer’s documentation.

## Slide 35: CO alarms and gas detectors
Regulatory requirements
BS EN 50292 and The Smoke and Carbon Monoxide Alarm (England) Regulations 2015 require:
CO alarms must be installed in any room containing a solid fuel-burning appliance.
In Scotland and Northern Ireland, CO alarms are required for all fuel types, including gas.
Alarms must be ceiling-mounted and at least 300mm from any wall.

## Slide 36: CO alarms and gas detectors
Regulatory requirements
Alternatively, if wall mounted, positioned at high level, higher than any door or window.
Located 1-3m horizontally from the appliance.
Comply with BS EN 50291-1:2018.
Have a minimum category B rating.
As a Gas Safe registered engineer, you should advise customers about CO alarm requirements even when not mandatory, as part of best practice safety guidance.

## Slide 37: CO alarms and gas detectors
Testing procedure
Press and hold the test button (should sound an alarm).
Check LED indicators function correctly.
Verify battery condition (if battery-powered).
Check manufacturing/installation date.
For advanced testing, use calibrated CO test gas.

## Slide 38: CO alarms and gas detectors
Replacement criteria
Must be replaced after 5-7 years (check manufacturer).
Replace immediately if test button fails.
Replace if physical damage is present.
Upgrade if not BS EN 50291 compliant.
Record replacement date on new alarm.
Document replacement in service records.

## Slide 39: Summary
You should now be able to:
List the steps for testing key safety devices in gas systems.
Identify when a device is faulty or out of tolerance.
Explain safe procedures for replacing safety-critical components.
Apply compliance checks using MI, GSIUR, and Gas Safe guidelines.

## Slide 40
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.