## Slide 1
Occupational Specialism: Gas Engineering
K1.11 Gas and the combustion process
PowerPoint 1.11b: Combustion analysis and trigger values

## Slide 2: Starter
You complete commissioning on a new boiler and print off this flue gas analysis:
CO = 32 ppm
CO₂ = 8.4%
O₂ = 6.5%
CO/CO₂ Ratio = 0.0038
Is this appliance burning safely?
Which values do you check first?
What would you do if CO was 400 ppm?

## Slide 3: Objectives
By the end of this session, you should be able to:
Use a flue gas analyser to measure combustion performance.
Interpret combustion readings: CO, CO₂, O₂, ratio.
Compare values against safe trigger points (IGEM/G/11).
Apply results to commissioning and servicing decisions.

## Slide 4: Combustion analysis and trigger values
Understanding combustion analysis is critical for ensuring gas appliances operate safely and efficiently.
This presentation explores how to properly measure, interpret and respond to combustion readings in accordance with industry standards.

## Slide 5: What is combustion analysis?
The essential tool
A combustion analyser is a sophisticated diagnostic instrument that measures the products of combustion in flue gases to determine if an appliance is operating safely and efficiently.
Modern electronic analysers typically display:
Oxygen percentage (% O₂), Carbon dioxide percentage (% CO₂), Carbon monoxide concentration (ppm CO), CO/CO₂ ratio (calculated), Flue temperature (°C), Combustion efficiency (%).
Most units provide printed records for documentation purposes.

## Slide 6: What is combustion analysis?
When analysis is required
Combustion analysis must be performed during:
Commissioning: To verify new installations meet safety standards
Servicing: To confirm ongoing safe operation
Fault diagnosis: To identify combustion-related issues.
Important: Analysers must be calibrated regularly in accordance with the manufacturer's instructions to ensure accurate readings.

## Slide 7: CO, CO₂, and O₂ values – what’s normal?
Typical combustion values for natural gas
Note: These ranges apply specifically to natural gas appliances. LPG and other fuels will have different acceptable parameters.
Parameter | Normal range | Significance
CO₂ | 7.5–9.0% | Indicates combustion completeness
O₂ | 4–7% | Reflects excess air for combustion
CO | < 50 ppm | Should be minimal (per MI)
CO/CO₂ Ratio | < 0.004 | Critical safety indicator
Efficiency | 88–94% | Higher is better (condensing)

## Slide 8: CO, CO₂, and O₂ values – what's normal?
Understanding the relationship
These values are interconnected and tell the complete combustion story:
High CO₂ + Low O₂: Good combustion but may indicate insufficient air if extreme
Low CO₂ + High O₂: Excess air diluting flue gases, potentially reducing efficiency
High CO + Normal CO₂: Incomplete combustion despite sufficient air (potential blockage or burner issue).
Critical safety note: The CO/CO₂ ratio is more important than absolute CO values, as it accounts for dilution effects and provides a more reliable indication of combustion quality.

## Slide 9: Interpreting the CO/CO₂ ratio
Maximum Safe Ratio = 0.004
Typically indicates acceptable combustion performance for most domestic appliances.
At Risk Threshold = 0.008
The point at which an appliance must be shut down as unsafe under IGEM/G/11.
Manufacturer Limit = 0.003
Some manufacturers specify stricter requirements in their instructions.

## Slide 10: Interpreting the CO/CO₂ ratio
The ratio explained
The CO/CO₂ ratio is calculated by dividing the CO reading (in ppm) by the CO₂ reading (in %) multiplied by 10,000.
For example:
32 ppm CO ÷ (8.4% CO₂ × 10,000) = 0.0038
< 0.004 (✓)
Acceptable combustion – appliance operating normally.
Record readings in documentation and Benchmark logbook.

## Slide 11: Interpreting the CO/CO₂ ratio
0.004–0.008 (⚠️)
Borderline combustion – requires investigation.
Service the appliance, clean components, retest.
> 0.008 (❌)
Unsafe combustion – appliance must be shut down.
Classify as At Risk (AR), investigate thoroughly before recommissioning.
Remember: Always consult the specific manufacturer's instructions, as some may specify more stringent limits than the general IGEM/G/11 guidance.

## Slide 12: Using the combustion analyser
Proper testing technique
Accurate combustion analysis requires following a precise methodology:
Ensure the analyser is calibrated and operating correctly
Purge the analyser prior to use
Allow appliance to reach normal operating temperature
Insert probe into the correct sampling point (test nipple)
Wait for readings to stabilise (typically 1-2 minutes)
Record all values: CO, CO₂, O₂, ratio, efficiency
Compare readings to manufacturer's specifications
Print results and attach to documentation.

## Slide 13: Using the combustion analyser
Remember
Never test an appliance before it reaches normal operating temperature.
Condensation or unburnt gas in a cold appliance can produce misleading readings.

## Slide 14: Using the combustion analyser
Common testing errors
Avoid these mistakes to ensure accurate results:
Testing too early during warm-up phase
Incorrect probe positioning or air leakage around probe
Using an uncalibrated or out-of-date analyser
Not allowing readings to stabilise
Testing with case panels removed (affects air/gas ratio)
Ignoring manufacturer-specific test procedures
Modern analysers can store multiple readings, allowing comparison between commissioning and subsequent services.

## Slide 15: IGEM/G/11 – Response based on readings
Industry standard response framework
The Institution of Gas Engineers and Managers document G/11 provides standardised guidance on how to respond to combustion analysis readings:
Ratio < 0.004 (✓)
Classification: Safe
Required action: Record readings in Benchmark logbook and complete normal commissioning/service documentation.
Documentation: Standard service record

## Slide 16: IGEM/G/11 – Response based on readings
Ratio 0.004-0.008 (⚠️)
Classification: Investigate
Required action: Perform full service, clean components, check air supply, retest after adjustments.
Documentation: Note investigation in service record.

## Slide 17: IGEM/G/11 – Response based on readings
Ratio > 0.008 (❌)
Classification: At Risk (AR)
Required action: Shut down appliance, attach warning label, explain to customer, document on Warning Notice.
Documentation: Complete RIDDOR if appropriate.

## Slide 18: IGEM/G/11 – Response based on readings
Ratio > 0.01 or CO > 350 ppm (❌)
Classification: Immediately Dangerous (ID)
Required action: Isolate gas supply, attach Danger Do Not Use warning, explain to customer, document on Warning Notice
Documentation: Complete RIDDOR reporting, inform Gas Safe Register
These risk classifications directly impact your legal responsibilities and documentation requirements under Gas Safe Register guidelines.

## Slide 19: Real-life comparison table
Appliance-specific combustion parameters
Different types of gas appliances have varying combustion characteristics and safety thresholds based on their design and application:
Appliance type | Expected ratio | CO Limit | CO₂ Range | O₂ Range
Combi Boiler (Fan-assisted) | ≤ 0.003 | < 50 ppm | 8.0-9.5% | 4.0-5.5%
System Boiler (Room-sealed) | ≤ 0.003 | < 50 ppm | 8.5-9.5% | 3.5-5.0%
Open-Flued Fire | ≤ 0.004 | < 80 ppm | 5.0-7.0% | 10.0-13.0%
Flueless Gas Heater | ≤ 0.002 | < 15 ppm | 3.5-4.5% | 14.5-16.0%
Water Heater (Instantaneous) | ≤ 0.0035 | < 75 ppm | 6.0-8.0% | 7.0-9.5%
Range Cooker | ≤ 0.004 | < 80 ppm | 5.5-7.5% | 8.0-11.0%

## Slide 20: Real-life comparison table
Key factors affecting limits
Several factors influence the variation in acceptable combustion parameters between different appliance types:
Flue type: Room-sealed vs open-flued vs flueless
Air supply: Fan-assisted vs natural draught
Combustion chamber: Sealed vs open design
Appliance location: Living space vs utility room
Usage pattern: Continuous vs intermittent operation.

## Slide 21: Real-life comparison table
Flueless appliances: Have the strictest CO limits because combustion products enter directly into the living space, requiring excellent combustion quality and adequate room ventilation.
Always consult the specific manufacturer's instructions, as their requirements may be more stringent than these general guidelines, particularly for high-efficiency and condensing appliances.

## Slide 22: Knowledge check
What's the maximum CO/CO₂ ratio allowed under IGEM/G/11?
0.004
0.040
4.000
0.0004
The maximum safe ratio is 0.0040, with 0.0080 being the At Risk threshold.

## Slide 23: Knowledge check
Which gas indicates inefficient or incomplete combustion?
Carbon monoxide (CO)
Nitrogen oxide (NOx)
Water vapour (H₂O)
Oxygen (O₂)
CO is produced when there's insufficient oxygen for complete combustion.

## Slide 24: Knowledge check
A reading of 9.5% CO₂ and 300 ppm CO gives a ratio of 0.0032. Is this safe?
Yes
No
The ratio is below 0.0040, so technically safe, but the high CO value warrants investigation even though the ratio is acceptable.

## Slide 25: Knowledge check
When should combustion analysis be performed during commissioning?
Immediately after first ignition
After 30 seconds of operation
When appliance reaches normal operating temperature
Only after adjusting the gas valve
Testing must be done at normal operating temperature to avoid misleading readings from condensation or incomplete combustion.

## Slide 26: Case studies: Interpreting real-world readings
Case 1: High CO, Normal CO₂
Readings:
CO: 250 ppm , CO₂: 8.6% , O₂: 5.2% , Ratio: 0.0291
Analysis: Despite normal CO₂ and O₂ levels, the extremely high CO and ratio (>0.0080) indicate serious combustion problems.
Diagnosis: This pattern typically indicates a partially blocked heat exchanger or contamination of the burner. The normal CO₂ shows sufficient gas and air are mixing, but combustion is incomplete.
Action: Classify as Immediately Dangerous (ID), isolate the appliance, issue a warning notice, and conduct a thorough inspection.

## Slide 27: Case studies: Interpreting real-world readings
Case 2: Low CO₂, Low CO
Readings:
CO: 12 ppm , CO₂: 5.2% , O₂: 11.4% , Ratio: 0.0023
Analysis: The ratio is safe, but the low CO₂ and high O₂ indicate excess air dilution.
Diagnosis: This pattern suggests possible air leaks in the combustion chamber or incorrect gas pressure. The appliance is safe but inefficient.
Action: Check gas pressure, inspect seals, verify fan operation, and adjust air/gas ratio if applicable.

## Slide 28: Case studies: Interpreting real-world readings
Case 3: High CO₂, High CO
Readings:
CO: 110 ppm , CO₂: 10.2% , O₂: 2.1% , Ratio: 0.0108
Analysis: The high CO₂ and low O₂ indicate insufficient air, resulting in elevated CO and an unsafe ratio.
Diagnosis: This pattern typically indicates restricted air intake, ventilation issues, or incorrect gas/air adjustment.
Action: Classify as Immediately Dangerous (ID), isolate the appliance, check the ventilation, and inspect the air intake path.

## Slide 29: Case studies: Interpreting real-world readings
Case 4: Borderline readings
Readings:
CO: 35 ppm , CO₂: 8.2% , O₂: 6.8% , Ratio: 0.0043
Analysis: The ratio is just above the 0.004 threshold but below 0.008, placing it in the "investigate" category.
Diagnosis: The appliance is showing early signs of combustion issues but isn't immediately unsafe.
Action: Service the appliance, clean the burner, check the gas pressure, and retest. Document findings and advise the customer about potential issues.

## Slide 30: Advanced troubleshooting with combustion analysis
Using patterns to diagnose issues
Experienced gas engineers can use combustion readings to pinpoint specific faults:
The relationship between readings often reveals more than individual values alone.
Reading pattern | Likely fault
High CO, High CO₂, Low O₂ | Insufficient combustion air
High CO, Normal CO₂/O₂ | Burner contamination
Low CO₂, High O₂, Low efficiency | Air leaks in combustion chamber
Fluctuating readings | Fan issues or intermittent faults
High CO at startup only | Ignition/flame establishment issues

## Slide 31: Advanced troubleshooting with combustion analysis
Common remedial actions
Based on combustion analysis, these remedial actions often resolve issues:
Burner cleaning: Removes deposits that cause poor combustion
Heat exchanger cleaning: Improves heat transfer and gas flow
Ventilation improvement: Ensures adequate combustion air
Gas pressure adjustment: Corrects air/gas ratio issues
Flue inspection: Identifies blockages or restrictions
Fan replacement: Resolves air supply problems.

## Slide 32: Advanced troubleshooting with combustion analysis
Never attempt to adjust combustion parameters beyond manufacturer specifications.
Modern appliances have precisely calibrated combustion settings that shouldn't be altered without specific guidance.

## Slide 33: Documentation and legal requirements
Recording combustion analysis
Proper documentation is legally required and provides evidence of safe working practices:
Benchmark logbook: Attach printed analyser results to the commissioning checklist
Service record: Note all combustion readings on service documentation
Warning notices: Complete appropriate Gas Safe Register documentation for At Risk or Immediately Dangerous situations
RIDDOR: Report dangerous gas fittings to the HSE when required.

## Slide 34: Documentation and legal requirements
Recording combustion analysis
All documents should include:
Date and time of testing
Full set of combustion readings
Analyser calibration date
Actions taken based on readings
Engineer's Gas Safe ID number.

## Slide 35: Documentation and legal requirements
Legal Implications
Proper combustion analysis and documentation protect both customers and engineers:
Provides evidence of compliance with Gas Safety Regulations
Demonstrates professional competence and due diligence
Creates an audit trail for future reference
Supports decisions to condemn unsafe appliances
May be critical evidence in case of incidents or investigations.
Gas Safe Register inspections frequently focus on combustion analysis records to verify proper working practices.

## Slide 36: Summary
You should now be able to:
Use a flue gas analyser to measure combustion performance.
Interpret combustion readings: CO, CO₂, O₂, ratio.
Compare values against safe trigger points (IGEM/G/11).
Apply results to commissioning and servicing decisions.

## Slide 37
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.