## Slide 1
Occupational Specialism: Gas Engineering
K1.11 Gas and the combustion process
PowerPoint 1.11c: Burners and air movement – simplex, duplex and ventilation devices

## Slide 2: Starter
Two gas appliances are fitted in a poorly ventilated cupboard:
A flueless space heater
A boiler with a fan-assisted burner
Prompt discussion:
Which appliance poses a greater risk?
What burner type might each appliance use?
How does the appliance draw in combustion air?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify types of gas burners (simplex, duplex) and their features.
Explain how burners influence flame stability and combustion.
Describe how ventilators and MVHR systems affect air supply.
Link burner performance to appliance safety and design.

## Slide 4: Burner types: simplex vs duplex
The physical design of burners significantly impacts flame characteristics and combustion efficiency. Simplex burners produce a single row of flames while duplex burners create multiple flame patterns for improved control.
Burner type | Description | Applications
Simplex | Single flame row or port, basic design with limited modulation capability | Domestic cookers, basic water heaters, simple space heaters
Duplex | Two flame rows or multi-stage burner design with improved modulation | Boilers, commercial equipment, advanced space heaters

## Slide 5: Burner types: simplex vs duplex
Key technical features
Burner port size and shape directly affect flame speed, stability and primary aeration
Aerated burners pre-mix air with gas before combustion
Non-aerated burners rely on secondary air drawn around the flame
Duplex burners allow for turndown ratios up to 5:1 compared to 2:1 for simplex
Flame rectification and ionisation sensing more effective with duplex designs.

## Slide 6: Burner types: simplex vs duplex
Engineering note
Simplex burners are characterised by lower cost and simpler controls but offer limited output modulation.
Duplex burners provide better flame spread, more precise modulation, and typically higher overall efficiency across load ranges.

## Slide 7: Burner air supply methods
Natural draught
Utilises thermal buoyancy effects to draw air naturally through the burner and flue system.
Relies on temperature differential and flue height to create draught.
Common in:
Traditional open-flued systems
Conventional boilers
Gas fires.

## Slide 8: Burner air supply methods
Fan-assisted
Employs a mechanical fan to create forced airflow through the combustion chamber, ensuring precise air-to-gas ratios regardless of external conditions.
Common in:
Room-sealed boilers
Modern combination appliances
High-efficiency systems.

## Slide 9: Burner air supply methods
Induced draught
A fan positioned at the flue outlet pulls combustion products out rather than pushing air in, creating negative pressure that draws air through the system.
Common in:
Some commercial boilers
Industrial heating systems
Specialised applications.

## Slide 10: Burner air supply methods
Flueless
Draws all combustion air directly from the room without mechanical assistance.
Requires substantial permanent ventilation provision to ensure safe operation.
Common in:
Domestic cookers
Flueless gas fires
Portable LPG heaters.

## Slide 11: Burner air supply methods
Critical safety point
Air supply must be consistent, clean and unobstructed.
Dust, lint, or grease accumulation can cause flame instability, incomplete combustion, and potentially dangerous conditions, including carbon monoxide production.
The engineer must consider the air supply method when commissioning or servicing an appliance, as it directly impacts combustion quality, efficiency, and safety.
Air supply faults are a leading cause of unsafe appliances and related incidents in the UK gas industry.

## Slide 12: Role of ventilators
Ventilators serve the critical function of ensuring gas appliances receive sufficient fresh air to maintain complete, clean combustion.
The design, sizing and positioning of ventilation is governed by specific British Standards and industry guidance documents.

## Slide 13: Role of ventilators
Types of ventilation
Fixed air vents
Permanent openings that cannot be closed or adjusted, typically required for open-flued or flueless appliances. Must provide direct access to outside air.
High/low level vents
Dual ventilation system with openings at both high and low positions to create natural circulation. Required for appliances in confined spaces or compartments.

## Slide 14: Role of ventilators
Types of ventilation
Mechanical fans
Powered ventilation systems that actively move air into or out of a space. May be interlocked with appliance operation for safety.
Passive grilles
Non-powered ventilation grilles that allow air movement through walls, doors or other structures. May include fire-rated or acoustic designs.

## Slide 15: Role of ventilators
Ventilation sizing factors
Appliance input rating - measured in kilowatts (kW)
Flue type - open-flued, room-sealed or flueless
Room volume - total space available for air circulation
Building air-tightness - newer buildings typically more airtight
Purpose of room - habitable vs non-habitable spaces
Installation location - internal vs external walls.

## Slide 16: Role of ventilators
Key guidance documents
IGEM/G/11 - Gas installations in educational establishments
BS 5440-2 - Installation and maintenance of flues and ventilation
Building Regulations Approved Document J
BS 6798 - Specification for installation of gas-fired boilers
Manufacturer's installation instructions.

## Slide 17: MVHR (Mechanical Ventilation with Heat Recovery)
MVHR systems are becoming increasingly common in new-build properties and energy-efficient retrofits.
They extract stale air from wet rooms (kitchen, bathrooms) and supply fresh filtered air to habitable rooms, recovering heat in the process.
Critical requirement
MVHR systems must never interfere with dedicated combustion air paths or flue systems. Gas Safe engineers must be particularly vigilant when working in properties with MVHR systems, especially when these have been retrofitted after gas appliance installation.

## Slide 18: MVHR (Mechanical Ventilation with Heat Recovery)
MVHR system characteristics
Whole-building ventilation approach for energy-efficient homes
Typically delivers 0.5-1.0 air changes per hour
Recovers 85-95% of heat from extracted air
Creates slight positive or negative pressure differentials
Incorporates filters to improve indoor air quality
Often computer-controlled with variable speeds
May include summer bypass mode for warmer months.

## Slide 19: MVHR (Mechanical Ventilation with Heat Recovery)
Gas safety implications
May create pressure differentials affecting flue performance
Can potentially compete with open-flued appliances for air
Not suitable for use with flueless appliances without a specific risk assessment
System failure could compromise combustion air supply
Maintenance regimes critical for ongoing safety
Commissioning must include spillage testing of all affected appliances.

## Slide 20: Extraction fans
Extraction fans, such as those used in bathrooms and kitchens, are designed to remove stale, humid, or contaminated air from indoor spaces and replace it with fresh air. Their primary purpose is to improve indoor air quality, prevent moisture-related damage, and support health and safety.
Critical requirement
Extraction fans must never interfere with dedicated combustion air paths or flue systems. Gas Safe engineers must be particularly vigilant when working in properties with extraction fans, especially when these have been retrofitted after gas appliance installation.

## Slide 21: Combustion impact of air supply faults
Undersized ventilation
Combustion effect: Insufficient oxygen for complete combustion, leading to increased CO production.
Visual signs: Yellow flame tips, sooting on the heat exchanger or around the burner, black deposits.
Instrument reading: CO/CO₂ ratio above 0.004, high CO readings in flue gas analysis.

## Slide 22: Combustion impact of air supply faults
Blocked air intake
Combustion effect: Restricted primary air leading to poor flame formation and unstable combustion.
Visual signs: Lifting flames, flame extinguishment, delayed ignition, condensation on cold surfaces.
Instrument reading: Low O₂ readings, fluctuating pressure readings, intermittent flame failure.

## Slide 23: Combustion impact of air supply faults
Fan failure
Combustion effect: Loss of forced air movement, possible flame impingement on the heat exchanger.
Visual signs: Lockout error codes, APS fault indication, repeated reset attempts.
Instrument reading: No differential pressure across APS terminals, PCB diagnostic codes.

## Slide 24: Combustion impact of air supply faults
MVHR back-pressure
Combustion effect: Disruption of natural draught, potential for flue gas spillage into the room.
Visual signs: CO alarm activation, inconsistent flame pattern, spillage during spillage test.
Instrument reading: Failed spillage test, CO detected in room air during operation.

## Slide 25: Combustion impact of air supply faults
Air supply faults represent a significant proportion of dangerous gas installations identified during routine safety checks.
When investigating combustion problems, the engineer must systematically evaluate all aspects of ventilation and air supply, as these issues may present intermittently depending on environmental conditions.
Engineering link
This connects directly to knowledge from K1.10 regarding Flame Supervision Devices (FSD), Air Pressure Switches (APS), and carbon monoxide alarms – all of which provide critical protection against air supply issues.

## Slide 26: Matching burners to appliance types
Selection criteria
Engineers must consider multiple factors when specifying or evaluating burner systems for different applications:
Heat output requirements (steady-state vs variable load)
Turn-down ratio needed (minimum to maximum output)
Installation location (ventilation availability)
Control complexity (basic vs advanced modulation)

## Slide 27: Matching burners to appliance types
Selection criteria
Engineers must consider multiple factors when specifying or evaluating burner systems for different applications:
Noise constraints (especially in residential settings)
Efficiency targets (standard vs high-efficiency)
NOx emission requirements (increasingly important)
Maintenance accessibility (service frequency)

## Slide 28: Matching burners to appliance types
Common appliance-burner pairings
The selection of burner type should always prioritise safety, followed by performance efficiency and control requirements. For replacement scenarios, engineers must ensure compatibility with existing ventilation and flue arrangements or upgrade these accordingly.
Appliance type | Typical burner | Air supply method
Combi Boiler | Duplex, pre-mix | Fan-assisted, room-sealed
Cooker Hob | Simplex, non-aerated | Flueless, room air
Decorative Gas Fire | Simplex, aerated | Open-flued or flueless
Instantaneous Water Heater | Simplex, naturally aspirated | Open-flued, natural draught
Commercial Boiler | Multi-stage duplex, pre-mix | Fan-assisted, induced draught
Condensing System Boiler | Duplex, fully modulating | Fan-assisted, room-sealed
LPG Camping Stove | Simplex, basic jets | Flueless, open air

## Slide 29: Knowledge check
Question 1
What is a key feature of a duplex burner?
Uses two different gases simultaneously
Has multiple flame ports or rows
Only works with LPG fuel supply
Cannot be modulated once installed
Correct answer: B. Duplex burners feature multiple flame ports or rows, allowing for improved modulation and more stable combustion across different output levels.

## Slide 30: Knowledge check
Question 2
What ventilation type is commonly used in tightly sealed modern homes?
Traditional chimney
Openable window
MVHR system
Passive floor vent
Correct answer: C. MVHR (Mechanical Ventilation with Heat Recovery) systems are increasingly common in modern airtight homes, providing controlled ventilation while recovering heat energy.

## Slide 31: Knowledge check
Question 3
Which appliance must not be used with MVHR without specific risk assessment?
Room-sealed boiler
B. Flueless space heater
C. Fan-assisted boiler
D. Electric cooker
Correct answer: B. Flueless space heaters must not be used with MVHR systems without specific risk assessment, as the MVHR might disrupt the ventilation required for safe operation of these appliances.

## Slide 32: Knowledge check
Additional assessment question
What would be your immediate action if you discovered a natural draught open-flued boiler installed in a room with an MVHR system and no dedicated combustion air supply?
Take a moment to formulate your answer before proceeding. Consider both immediate safety concerns and longer-term remedial options.

## Slide 33: Knowledge check
Additional assessment question
What would be your immediate action if you discovered a natural draught open-flued boiler installed in a room with an MVHR system and no dedicated combustion air supply?
The correct approach would be to immediately assess the risk of carbon monoxide poisoning, perform a spillage test under worst-case conditions, and potentially classify the installation as "At Risk" or "Immediately Dangerous" depending on test results. Longer-term solutions might include a dedicated combustion air supply, replacement with a room-sealed appliance, or modifications to the MVHR system.

## Slide 34: Adventitious air
Adventitious air refers to the incidental or natural infiltration of air into a room, which can contribute to the overall ventilation available for combustion appliances. For appliances rated up to 7 kW net heat input, this air is often considered sufficient to meet basic combustion air requirements without the need for additional permanent ventilation.
In domestic settings, particularly with open-flued appliances, BS 5440-2 allows for an assumed provision of 35 cm² free area of adventitious ventilation per room. This is typically derived from gaps around doors, windows, and building fabric leakage.

## Slide 35: Air supply calculation
Ventilation requirements
For open-flued appliances in a room, free area of permanent air vent(s) should be:
5cm² x net input rating (kW)
Example calculation
For a domestic open-flued boiler with 24kW input:
24-7= 17 x 5 = 85 cm²
Therefore, a permanent air vent with at least 85 cm² free area is required.

## Slide 36: Air supply calculation
Compartment ventilation
For an open-flued appliance in a compartment:
High-level vent: 5 cm² per kW
Low-level vent: 10 cm² per kW

## Slide 37: Practical considerations
When calculating and implementing ventilation requirements:
Account for the effective free area of grilles (typically 50-70% of gross area)
Ensure vents cannot be easily blocked by furniture or curtains
Position vents to minimise draughts in occupied areas
For multiple appliances, add the individual ventilation requirements
Check for any special requirements in the manufacturer's instructions
Consider external factors that may affect ventilation (e.g. wind exposure)
Consider the minimum/maximum aperture for ventilation grill size, “must admit a 5mm ball bearing but not a 10mm ball bearing”.

## Slide 38: Flame characteristics and burner performance
Different flame appearances indicate specific combustion conditions. Engineers must be able to identify normal and abnormal flame patterns to diagnose potential issues with burners and air supply.
Flame type | Appearance | Indicates
Normal | Blue flame with well-defined inner cone | Correct air/gas ratio, complete combustion
Yellow Tipping | Blue flame with yellow tips | Insufficient primary air, partial incomplete combustion
Lazy Flame | Soft, indistinct yellow flame | Severe primary air deficiency, CO production likely
Lifting Flame | Flame lifting away from burner ports | Excessive primary air, potential flame instability
Floating Flame | Flame detached from burner | Excessive gas pressure or air flow, dangerous condition
Extinction | Flame extinguishes during operation | Air starvation, excessive draught, or control fault

## Slide 39: Flame characteristics and burner performance
Associated gas pressures
Proper burner performance depends on correct gas pressure:
Natural gas (G20): 20 mbar nominal supply pressure
LPG (G31): 37 mbar nominal supply pressure
Working pressure: typically 15-20 mbar for natural gas appliances
Burner pressure: varies by appliance - always check manufacturer's data.

## Slide 40: Advanced burner technologies - low-nox burners
Modern gas appliances increasingly incorporate low-NOx burner technology to reduce harmful emissions:
Utilise pre-mix combustion for precise air-gas control
Often feature mesh or ceramic surface burners
Operate at lower flame temperatures to reduce thermal NOx
May incorporate staged combustion techniques
Typically achieve NOx levels below 40 mg/kWh
Meet Class 5 requirements under EN 15502
Critical for compliance with ErP Directive (2009/125/EC).

## Slide 41: Advanced burner technologies
Modulating burner systems
Advanced modulation technologies provide significant benefits:
Wide turndown ratios (up to 10:1 in premium systems)
Electronically controlled gas valves for precise adjustment
Variable speed fans matched to the required output.

## Slide 42: Advanced burner technologies
Modulating burner systems
Advanced modulation technologies provide significant benefits:
Oxygen sensing for real-time combustion optimisation
Improved seasonal efficiency through reduced cycling
Enhanced comfort through consistent heat output
Reduced component wear from frequent on/off cycling
Lower noise through gradual power changes.

## Slide 43: Case study: air supply failure analysis
Incident summary
A family of four reported frequent headaches and dizziness in their newly renovated home. The property had recently undergone significant energy efficiency improvements, including new windows, external wall insulation, and installation of an MVHR system. A Gas Safe engineer was called to investigate.

## Slide 44: Case study: air supply failure analysis
Investigation findings
Initial assessment
An engineer discovered an open-flued gas fire in the living room showing signs of incomplete combustion with yellow flames and sooting.
Testing conducted
Spillage testing revealed products of combustion entering the room when the MVHR system was operating at high speed. CO levels in the room rose to 35ppm during testing.

## Slide 45: Case study: air supply failure analysis
Investigation findings
Root cause analysis
The MVHR system was creating negative pressure in the living room, competing with the natural draught of the open-flued gas fire. Renovation work had sealed previous air infiltration paths.
Remedial action
The engineer classified the installation as "Immediately Dangerous" and disconnected the gas fire with the customer’s permission. Before reconnection, a dedicated permanent air vent was recommended.

## Slide 46: Case study: air supply failure analysis
Contributing factors
Energy efficiency measures had dramatically reduced natural ventilation
MVHR system designed without consideration of the gas fire
No dedicated combustion air vent installed for the open-flued appliance
Original installation complied with regulations before renovation
Occupants are unaware of ventilation requirements when making changes
No carbon monoxide alarm installed in the living room
Symptoms of CO exposure initially mistaken for seasonal illness.

## Slide 47: Case study: air supply failure analysis
Learning points
Energy efficiency measures can significantly impact existing gas installations
Open-flued appliances require careful consideration in airtight properties
MVHR systems must be professionally designed with gas appliances in mind
CO alarms are essential safety devices, especially with open-flued systems.

## Slide 48: Summary and key takeaways
Burner types
You can now identify simplex and duplex burners, understand their distinctive features, and explain where each type is typically used in gas appliances.
Air supply methods
You can describe how combustion air is delivered through natural draught, fan-assisted, induced draught, and flueless systems, and the implications for installation.
Ventilation requirements
You understand the critical role of ventilation, can calculate required free areas, and recognise the impact of different vent types on combustion performance.

## Slide 49: Summary and key takeaways
MVHR considerations
You can explain how MVHR systems interact with gas appliances, identify potential risks, and specify appropriate safety measures for different installation scenarios.
Safety assessment
You can recognise the visual signs of air supply problems, understand the associated risks, and take appropriate action when encountering unsafe installations.
Remember: Ensuring adequate combustion air supply is one of the most fundamental aspects of gas safety. Many dangerous incidents could be prevented through proper understanding and application of these principles.

## Slide 50: Summary
You should now be able to:
Identify types of gas burners (simplex, duplex) and their features.
Explain how burners influence flame stability and combustion.
Describe how ventilators and MVHR systems affect air supply.
Link burner performance to appliance safety and design.

## Slide 51
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.