## Slide 1
Occupational Specialism: Gas Engineering
K1.11 Gas and the combustion process
PowerPoint 1.11e: Gas behaviour – flammability, freezing, density, Wobbe Number

## Slide 2: Starter
Scenario: A leak occurs in an LPG installation in a basement. No CO alarms are sounding, but there's a strong gas smell near the floor.
Discussion prompts
Why is this more dangerous than a similar leak upstairs with natural gas?
What gas property is causing this behaviour?
What actions should the engineer take?

## Slide 3: Objectives
By the end of the session, you should be able to:
Define flammability limits and their impact on gas safety.
Explain the significance of freezing temperatures and relative density.
Interpret Wobbe Numbers and gas interchangeability.
Apply these properties to safe system design and maintenance.

## Slide 4: Flammability limits (UEL / LEL)
⚠️ Outside the flammability range = no ignition
Within range + spark = explosion risk
Gas | LEL (%) | UEL (%) | Notes
Methane | 5.0 | 15.0 | Narrow range
Propane | 2.1 | 9.5 | Wider range, higher risk
Butane | 1.8 | 8.4 | Ignites easily in confined space

## Slide 5: Flammability limits (UEL / LEL)
Definition
The range of gas-air mixtures that can ignite if a spark occurs. Gas must be mixed with air in specific proportions to burn or explode.
Lower Explosive Limit (LEL): Minimum concentration of gas in air that will burn
Upper Explosive Limit (UEL): Maximum concentration of gas in air that will burn
Outside these limits, the mixture is either too lean (below LEL) or too rich (above UEL) to ignite.

## Slide 6: Understanding flammability limits in practice
Why flammability limits matter
Flammability limits are critical for purging operations, leak testing, and risk assessment. They determine:
Safe working environments during installation and maintenance
Ventilation requirements to keep gas concentrations below LEL
Operational parameters for gas appliances and detection systems.

## Slide 7: Understanding flammability limits in practice
Safety implications
LPG gases have lower LELs than natural gas, making them more hazardous:
They ignite at lower concentrations (1.8-2.1% vs 5.0%)
They form explosive mixtures more readily in confined spaces
Gas detection equipment must be calibrated specifically for the gas type.

## Slide 8: Understanding flammability limits in practice
Industry standards
IGEM/UP/1B and BS 6891 specify protocols for:
Purging systems to ensure gas-air mixtures remain outside flammable range
Testing procedures that minimise explosion risk
Emergency procedures during suspected leaks
Engineers must understand these limits to determine safe operating procedures, especially when commissioning, decommissioning, or testing gas installations.

## Slide 9: Freezing temperatures
Gas | Freezing Point | Implication
Methane | −182°C | No freezing issues in UK climate
Propane | −42°C | Vaporises reliably in UK winters
Butane | −0.5°C | Freezes in mild cold conditions

## Slide 10: Freezing temperatures
Problem
Butane cylinders may fail to vaporise in cold ambient temperatures:
Appliances won't work properly in winter
Gas pressure drops as temperature falls
Below freezing point, liquid gas cannot convert to vapour
Results in pilot light failure and appliance shutdown.

## Slide 11: Freezing temperatures
LPG installation consideration
Always check location conditions for winter reliability.
Butane should not be used in unheated outdoor spaces in the UK during the winter months.
Due to its lower freezing point, propane is the appropriate LPG choice for reliable winter operation in outdoor or unheated locations (sheds, caravans, boats).

## Slide 12: Relative density (specific gravity)
Definition: How heavy a gas is compared to air (Air = 1.0)
Methane's low density means it typically rises and disperses through ceiling vents, while LPG gases sink and accumulate in low-lying areas, creating potentially dangerous pockets of gas.
Gas | Relative Density | Behaviour
Methane | 0.55 | Rises when leaked ✅
Propane | 1.52 | Sinks to low points ⚠️
Butane | 2.00 | Very heavy – cellars = danger

## Slide 13: Relative density (specific gravity)
Implications:
Ventilation must be appropriate for gas type (high for natural gas, low for LPG)
Leak detection strategy changes based on gas density
Flue terminal placement must account for gas behaviour
Room-sealed appliances help reduce risk by isolating combustion from room air
Basement installations require special consideration with LPG systems.

## Slide 14: Safety implications of relative density
Natural gas (Methane)
With a relative density of 0.55, natural gas is lighter than air and rises when leaked.
Ventilation requirements: High-level vents and extraction.
Detection: Gas detectors positioned at ceiling level.
Risk areas: Enclosed ceiling spaces, roof voids, upper floors.

## Slide 15: Safety implications of relative density
LPG - Propane
With a relative density of 1.52, propane is heavier than air and sinks when leaked.
Ventilation requirements: Low-level vents essential.
Detection: Gas detectors positioned at floor level.
Risk areas: Basements, service ducts, under-floor spaces.

## Slide 16: Safety implications of relative density
LPG - Butane
With a relative density of 2.00, butane is significantly heavier than air and rapidly sinks when leaked.
Ventilation requirements: Enhanced low-level ventilation.
Detection: Multiple low-level detectors recommended.
Risk areas: Extreme danger in below-ground installations.
Not permitted in basement installations by IGEM/UP/1B.

## Slide 17: Safety implications of relative density
Understanding relative density is crucial for proper risk assessment, ventilation design, and leak detection strategies.
Engineers must consider these properties when designing systems and specifying detection equipment.

## Slide 18: What Is the Wobbe Number?
Definition
The Wobbe Number (WN) measures the interchangeability of different gases in combustion equipment.
It indicates whether gases will deliver similar heat outputs through the same burner without adjustment.
Gas | CV (MJ/m³) | RD | WN (approx)
Natural Gas | 38.76 | 0.55 | 52.2
Propane | 93.2 | 1.52 | 75.5

## Slide 19: What Is the Wobbe Number?
Practical application
Similar Wobbe Numbers mean gases can be interchanged without burner adjustment
Significant differences in WN cause combustion problems:
Flame lift-off (WN too high)
Incomplete combustion (WN too low)
Yellow flame tips and carbon monoxide production
Appliance overheating or underperformance.
⚠️ Appliances must not be converted from NG to LPG (or vice versa) unless approved and specifically adjusted by a qualified engineer.

## Slide 20: Wobbe Number and gas interchangeability
UK gas grid standards
The UK gas network maintains strict Wobbe Number requirements:
Natural gas must be within 47.2 - 51.41 MJ/m³ (GS(M)R standards)
Tight tolerances ensure consistent appliance performance
Grid operators blend gases to maintain specification
Future hydrogen blends will require careful Wobbe Number management.

## Slide 21: Wobbe Number and gas interchangeability
Appliance conversion
When changing gas types, appliances require specific modifications:
Injector size must be changed (smaller for LPG)
Air/gas ratio must be adjusted
Burner pressure settings recalibrated
Conversion must follow the manufacturer's instructions
Only attempt with approved conversion kits.

## Slide 22: Wobbe Number and gas interchangeability
Safety implications
Incorrect Wobbe Number matching leads to:
CO production due to incomplete combustion
Sooting and appliance damage
Flame instability and potential flashback
Overheating or insufficient heating
Premature appliance failure
Voiding of manufacturer warranties.

## Slide 23: Wobbe Number and gas interchangeability
Engineers must verify that appliances are suitable for the gas supply and properly adjusted according to the Wobbe Number of the gas being used.
This is particularly important when working on imported appliances or in areas with mixed gas supplies.

## Slide 24: Real-world implications
Flammability range
Influences safe leak testing and purging procedures. Engineers must:
Ensure adequate ventilation during purging
Follow specific purging procedures based on gas type
Use appropriate test equipment calibrated for specific gases
Apply stricter controls when working with LPG systems.

## Slide 25: Real-world implications
Freezing temperature
Affects LPG location and winter performance:
Propane must be used for outdoor installations
Butane is suitable only for indoor or heated locations
Cylinder sizing must account for vaporisation rates at low temperatures
Multiple smaller cylinders may outperform one large cylinder in cold conditions.

## Slide 26: Real-world implications
Relative density
Guides the flue terminal placement and ventilation design:
LPG requires low-level ventilation and leak detection
Natural gas requires high-level ventilation
LPG cannot be installed in basements or below ground level
Drainage and topography must be considered for external LPG installations.

## Slide 27: Real-world implications
Wobbe Number
Determines compatibility and appliance calibration:
Specific injector sizes for different gas types
Pressure settings must match gas properties
Flame stability depends on correct Wobbe matching
Regional gas composition variations may require adjustments.

## Slide 28: Case study: LPG in off-grid applications
Rural property installation challenges
Off-grid properties in the UK rely heavily on LPG for heating and cooking. Understanding gas properties is critical for these installations.
Consider a remote farmhouse in North Yorkshire with the following requirements:
Central heating and hot water system
Cooking range and gas hob
Outdoor workshop heating
Winter temperatures are frequently below freezing.
The engineer must apply knowledge of gas properties to design a safe and effective system that functions year-round.

## Slide 29: Case study: LPG in off-grid applications
Engineering solutions
Based on gas properties, the engineer should:
Select propane (not butane) due to freezing temperatures
Position tank above ground level with consideration for density (no valleys or depressions)
Install low-level ventilation in all enclosed spaces containing gas appliances
Use specifically designed LPG appliances with correct Wobbe Number compatibility
Fit low-level gas detection in the property due to LPG's high density
Specify appropriate pipe sizing to account for different flow characteristics.

## Slide 30: Wobbe Number and future gas supplies
Hydrogen blending
The UK is exploring hydrogen blending into the natural gas network as part of decarbonisation:
Up to 20% hydrogen blend being tested
Hydrogen has a Wobbe Number of 48 MJ/m³
Blending changes the Wobbe Number of delivered gas
Most existing appliances can handle up to 20% blend without adjustment.

## Slide 31: Wobbe Number and future gas supplies
Hydrogen blending
Engineers need to understand how these changes impact:
Appliance performance and safety
Combustion characteristics
Ventilation requirements
Detection systems.

## Slide 32: Wobbe Number and future gas supplies
International LNG imports
The UK increasingly relies on imported Liquefied Natural Gas (LNG):
Different composition from North Sea gas
Varying Wobbe Numbers between 48-53 MJ/m³
Requires gas processing to match UK specifications
Occasional need for "ballasting" with nitrogen to lower Wobbe Number.
The GS(M)R regulations specify that gas within UK networks must maintain Wobbe Number within tight limits to ensure appliance safety and performance.

## Slide 33: Key points
Flammability limits
Understanding LEL and UEL for different gases is critical for safety during installation, maintenance, and emergency response.
Natural gas: 5-15%
Propane: 2.1-9.5%
Butane: 1.8-8.4%

## Slide 34: Key points
Freezing temperatures
Critical for LPG installations, especially in unheated or outdoor locations.
Methane: -182°C
Propane: -42°C
Butane: -0.5°C

## Slide 35: Key points
Relative density
Determines gas behaviour in leaks and ventilation requirements.
Methane: 0.55 (rises)
Propane: 1.52 (sinks)
Butane: 2.00 (sinks rapidly)

## Slide 36: Key points
Wobbe Number
Essential for determining gas interchangeability and appliance compatibility.
Natural gas: ~52 MJ/m³
Propane: ~76 MJ/m³
Requires specific appliance design
As a gas engineer, understanding these properties is fundamental to ensuring safe, efficient installations. Your knowledge directly impacts the safety of customers and the reliability of gas systems under various conditions.

## Slide 37: Summary
You should now be able to:
Define flammability limits and their impact on gas safety.
Explain the significance of freezing temperatures and relative density.
Interpret Wobbe Numbers and gas interchangeability.
Apply these properties to safe system design and maintenance.

## Slide 38
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.