## Slide 1
Occupational Specialism: Gas Engineering
K1.14 Types of ventilation in relation to gas
PowerPoint 1.14c: Applied design, installation and inspection of ventilation systems

## Slide 2: Starter
A homeowner installs a gas fire in a small, sealed room. No air vents are visible.
What issues might this cause during use?
Write down 2 possible risks and suggest what should have been considered.

## Slide 3: Objectives
By the end of this session, you should be able to:
Recall key design rules for air vents and grilles.
Explain correct positioning based on appliance type and room layout.
Identify common installation faults through visual inspection.
You might also be able to:
Evaluate an installation against Building Regs and MI.
Propose rectification steps for poor ventilation setups.

## Slide 4: Key design considerations
Effective ventilation design ensures gas appliances operate safely and efficiently. It must take into account multiple interrelated factors:
1. Room size, volume, and air permeability
The available room volume determines whether sufficient adventitious air is available.
New, airtight dwellings may require increased permanent ventilation.
Reference: Approved Document J outlines permeability thresholds (e.g. ≤ 5 m³/h·m² requires additional ventilation).

## Slide 5: Key design considerations
2. Appliance location
The position of the appliance affects airflow and heat dissipation.
Common installation zones include:
  Kitchens: Must not rely on adventitious air; ventilation and spillage testing are critical
  Cupboards/compartments: Require both high and low level vents or manufacturer-specified clearance
  Lofts or roof spaces: Must be assessed for air availability and insulation coverage.

## Slide 6: Key design considerations
3. Appliance type
Each appliance type has specific ventilation needs:
Appliance type | Ventilation need
Open Flued (Type B) | Requires combustion air from the room or external vent
Room Sealed (Type C) | No room air required – air and flue ducts are sealed
Flueless (Type A) | Requires significant permanent ventilation – combustion products are released into the room

## Slide 7: Key design considerations
4. Ventilation source
Natural ventilation: Fixed openings to outside (e.g. air bricks, grilles).
Mechanical ventilation: Extract or supply fans – must be carefully balanced to avoid negative pressure.
Combination systems: Where both are used, ensure one does not impair the other’s function.

## Slide 8: Key design considerations
5. Grille positioning
Low-level vents are used to admit cooler, denser fresh air (especially for LPG installations).
High-level vents are used to expel warm air or allow buoyant gases to escape.
Grilles must provide the required free air area, not just a large physical size.

## Slide 9: Key design considerations
Guidance and compliance references
Approved Document J – Building Regulations for combustion appliances and ventilation.
IGEM/G/11 – Procedures for identifying and classifying unsafe gas situations.
Manufacturer’s Instructions (MI) – Always follow the specified ventilation and clearance requirements.
BS 5440-2 is the British Standard that provides guidance on the ventilation requirements for gas appliances..

## Slide 10: Grille and ventilation component types
1. Fixed wall grilles
Material: Metal or plastic
Function: Permanent openings for combustion air or compartment cooling
Compliance: Must have a known free air area
Note: Must not be closeable or obstructed

## Slide 11: Grille and ventilation component types
2. Air bricks
Material: Terracotta or plastic
Function: Built into external walls to provide fixed ventilation
Use: Often paired with sleeve or duct for through-wall ventilation
Caution: Check for insect mesh or blockage

## Slide 12: Grille and ventilation component types
3. Louvre panels
Design: Angled slats to allow airflow while reducing water ingress
Location: Internal cupboard or compartment doors
Application: Used to create high/low-level ventilation in enclosures
Check: Confirm free area, not just physical size

## Slide 13: Grille and ventilation component types
4. Mechanical fan ducts (with backdraft shutter)
Type: Extract or supply fans
Feature: Include non-return shutters to prevent unwanted draughts
Use: In mechanical ventilation or MVHR systems
Caution: Must not create negative pressure near open-flued appliances

## Slide 14: Grille and ventilation component types
5. Trickle vents in windows
Built-in feature: Found in double-glazed window frames
Function: Provide background ventilation in modern airtight buildings
Limitation: Not suitable as the sole means of combustion ventilation
Standard: Often required for compliance with Part F of the Building Regulations

## Slide 15: Room layout examples
Example 1: Bathroom with fan-assisted flueless heater
Scenario: A flueless gas heater is installed on the bathroom wall. The room has a small high-level window and an extractor fan.
What to consider:
Flueless appliances discharge combustion products into the room
Bathrooms are high-humidity areas with limited air movement
Combustion air must be permanently available – extract fans may create negative pressure.

## Slide 16: Room layout examples
Example 1: Bathroom with fan-assisted flueless heater
Key questions:
Is permanent low-level ventilation present?
Is the room volume large enough?
Is the appliance even suitable for bathroom installation under MIs and Part J?

## Slide 17: Room layout examples
Example 2: Kitchen with a combination boiler
Scenario: A room-sealed combination boiler is wall-mounted above a worktop. A powerful cooker hood extractor is located 500 mm away.
What to Consider:
Room-sealed boilers draw air from outside, but still must be installed with minimum clearance from fans
Extractors can interfere with flue termination
Combustion performance may be affected if the flue is short or poorly positioned.

## Slide 18: Room layout examples
Example 2: Kitchen with a combination boiler
Key questions:
Does the fan interfere with the flue terminal zone?
Is the flue termination distance compliant with MIs and Building Regs?
Have spillage/flue flow tests been conducted?

## Slide 19: Room layout examples
Example 3: Cupboard with a vertical flue boiler
Scenario: A room sealed heat-only boiler is installed in an enclosed cupboard under the stairs. One grille is at the high level.
What to consider:
Enclosures require both high and low-level ventilation
Grilles must have known free area
Room-sealed appliances may require cooling air even if sealed from the room.

## Slide 20: Room layout examples
Example 3: Cupboard with a vertical flue boiler
Key questions:
Is there a low-level grille?
Are the grilles free of obstruction?
Are the manufacturer’s clearance zones maintained?

## Slide 21: Visual inspection procedures
According to IGEM/G/11 and MI:
Check vent size and clear opening (not blocked)
Look for signs of condensation or CO build-up
Ensure air flow paths are not obstructed (e.g., behind furniture)
Confirm that installed vents match appliance requirements.
⚠️ Ventilation faults often go unnoticed until appliances misfire.

## Slide 22: Common faults in ventilation systems
Blocked grilles (painted over or furniture-covered)
Undersized vent area
Shared vents between rooms
Fans causing negative pressure near open flued appliances
No cross-ventilation in sealed area
Reference: Part J Appendix C & IGEM G/11 Visual Checklist

## Slide 23: Fault-finding activity
Scenario: Simon reports that his flueless gas fire keeps cutting out.
What might be wrong?
What checks should you perform visually?
How would you confirm the ventilation is compliant?

## Slide 24: Summary
You should now be able to:
Recall key design rules for air vents and grilles.
Explain correct positioning based on appliance type and room layout.
Identify common installation faults through visual inspection.
You might also be able to:
Evaluate an installation against Building Regs and MI.
Propose rectification steps for poor ventilation setups.

## Slide 25
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.