## Slide 1
Occupational Specialism: Gas Engineering
K1.6 Types of components and their suitability for different appliances and types of systems
PowerPoint 1.6a: Introduction to gas components

## Slide 2: Starter
Today we're going to explore what takes place inside a gas appliance the moment it's switched on, a process that’s critical to both safety and performance in gas engineering.
Let’s start by thinking about these two questions:
What happens inside a gas appliance when it’s turned on?
What do you think is actually ‘burning’?
Take a minute to discuss with a partner or jot down your thoughts. We’ll share ideas before diving into the science behind combustion.

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify a range of key components used in domestic gas appliances.
Describe their general purpose in gas systems.
Classify appliances based on fuel and system type.
Interpret manufacturer guidance when selecting components.
You might also be able to:
Evaluate the consequences of selecting an unsuitable component.
Link component operation to system behaviour and safety status (AR/ID).

## Slide 4: What is a gas appliance component?
A component is a part of the appliance or system that performs a specific function related to control, safety, sensing or operational performance.
Understanding components is critical for installation, servicing, and fault diagnosis in gas engineering.

## Slide 5: What is a gas appliance component?
Component classifications
Mechanical: Physical parts that control gas flow (valves, regulators).
Electrical: Components that use electricity (switches, relays).
Electronic: Circuit-based components (PCBs, microprocessors).
Pneumatic: Air pressure-operated components (diaphragms).
All components must be suitable for their application and comply with UK gas safety regulations and manufacturer specifications.

## Slide 6: What is a gas appliance component?
Component roles
Control: Regulate gas flow, temperature, or operation sequence.
Safety: Prevent unsafe conditions or shut down system.
Measurement: Monitor system parameters (temperature, pressure).
Intelligence: Process information and control system behaviour.

## Slide 7: Purpose of components in gas systems
Each component must be suitable for the specific system and appliance it is installed in. UK Gas Safe engineers must ensure all components meet appropriate British Standards and are compatible with the manufacturer's specifications.

## Slide 8: Purpose of components in gas systems
Purpose | Example component | Explanation
Control | Gas valve | Opens/closes gas flow; may modulate flow rate based on demand
Monitor | Thermistor | Senses temperature to provide feedback for modulating burners and safety controls
Safety | Flame supervision device (FSD) | Detects presence of flame to prevent release of unburnt gas; mandatory safety device
Communication | Printed Circuit Board (PCB) | Manages signals between components and controls appliance behaviour sequences
Air/Gas Mix | Fan & ratio valves | Ensures correct combustion mixture for efficient and safe burning
Pressure Regulation | Gas pressure regulator | Maintains correct gas pressure for safe and efficient operation
Ignition | Spark generator/electrode | Creates spark to ignite gas when required by control system

## Slide 9: Natural gas vs LPG systems
UK gas engineers must be qualified for both natural gas and LPG work, understanding the critical differences between them.
Component selection must match the fuel type due to differing pressures, densities and combustion characteristics.

## Slide 10: Natural gas vs LPG systems
Never use components designed for natural gas in LPG systems (or vice versa) unless specifically designated for both by the manufacturer.
This is a critical safety consideration for UK gas engineers.
Feature | Natural Gas (NG) | LPG (Propane/Butane)
Supply Method | Piped from mains | Stored in cylinders/tanks
Pressure Range | 21 mbar (domestic) | 37 mbar (propane) / 28 mbar (butane)
Calorific Value | ~39.5 MJ/m³ | ~93.2 MJ/m³ (propane)
Component Differences | Larger jets/orifices, valves tuned for lower calorific gas | Smaller jets, tighter sealing valves, higher pressure ratings
UK Safety Standards | BS 6891 | BS 5482

## Slide 11: Types of appliances
Boilers
Central heating and domestic hot water. May be combination, system, or regular types.
Available as sealed or open-flued systems. Most common domestic gas appliance in UK properties.
Water heaters
Instantaneous or storage types. Provides hot water only, without central heating function.
Less common in modern UK installations but still found in older properties.

## Slide 12: Types of appliances
Cookers/Ovens
Domestic cooking appliances with multiple burners.
Often have separate components for hob, grill and oven functions.
Common in UK homes with varied safety requirements.
Space heaters
Wall-mounted or free-standing units for room heating.
Decorative or radiant heating units.
May be radiant, inset, outset, convector or flueless types.
Require specific safety components including FSDs and ODS systems
Subject to specific ventilation requirements under UK regulations.

## Slide 13: Types of gas systems
Flue system types:
Open flue: Uses air from room for combustion, products exit via flue.
Room sealed: Combustion circuit sealed from living space.
Balanced flue: Air intake and combustion products exit through same terminal.
​

## Slide 14: Types of gas systems
Air supply methods:
Natural draught: Relies on convection for flue operation.
Mechanical draught: Uses fan to assist removal of combustion products.
​

## Slide 15: Types of gas systems
Air supply methods:
The system type directly influences component selection requirements:
Fans required for mechanical draught systems.
Air Pressure Switches (APS) required for fan-flued systems.
Oxygen Depletion Sensors (ODS) for flueless appliances.
Different gas valve specifications based on pressure requirements.
​

## Slide 16: Using Manufacturer’s Instructions (MI)
Manufacturer's Instructions provide critical information that must be followed by UK Gas Safe engineers.
The Gas Safety (Installation and Use) Regulations make reference to following manufacturer's instructions as a legal requirement.

## Slide 17: Using Manufacturer’s Instructions (MI)
MIs provide:
Detailed wiring schematics.
Component specifications and tolerances.
Servicing guidance and intervals.
Safety notes and classification information.
Replacement part numbers and compatibility.
Commissioning procedures and parameters.

## Slide 18: Using Manufacturer’s Instructions (MI)
Engineers must not deviate from MIs unless explicitly stated it's safe to do so.
Non-compliance can invalidate warranties, create unsafe conditions, and potentially lead to prosecution.
Critical Safety Note
A multiblock valve rated for Natural Gas cannot be substituted on an LPG boiler without explicit confirmation in the manufacturer's instructions.
Such substitutions can lead to dangerous conditions and are prohibited under UK gas regulations.

## Slide 19: Using Manufacturer’s Instructions (MI)
Scenario: Ash fits a fan that looks similar to the original but doesn't check the MI. The appliance begins short-cycling. Why might that happen?
This scenario illustrates the importance of checking specifications - incorrect fan pressure ratings or electrical characteristics can cause operational issues and potentially dangerous conditions.

## Slide 20: Consequences of unsuitable components
Issue | Component Mismatch | Result | UK Safety Classification
Incorrect valve pressure | NG valve in LPG appliance | Overfuelled combustion, risk of explosion, CO production | Immediately Dangerous (ID)
Wrong thermistor rating | Domestic temp probe in commercial plant | Poor modulation, lockouts, inefficient operation | At Risk (AR)
Missing safety switch | No APS on fan-assisted flue | Uncontrolled combustion, potential flue gas spillage | Immediately Dangerous (ID)
Overloaded PCB | Incorrect fan draw or incorrect earthing | Burnout, non-start, electrical hazard | At Risk (AR) or ID
Incorrect burner jets | NG jets in LPG appliance | Sooting, incomplete combustion, CO production | Immediately Dangerous (ID)
Non-compatible seals | Standard O-rings where high-temp required | Gas leakage when hot, intermittent faults | At Risk (AR) or ID

## Slide 21: Consequences of unsuitable components
These classifications link directly to the Gas Industry Unsafe Situations Procedure (GIUSP), which is a key document for UK Gas Safe engineers.
We will cover this in more detail in future sessions.
Selecting unsuitable components can have serious legal implications under the Gas Safety (Installation and Use) Regulations, potentially leading to prosecution, especially if incidents occur.

## Slide 22: Component evolution and innovation
1970s-1980s
Mechanical controls dominated: bimetallic strips, mechanical timers, pilot lights with thermocouples.
Minimal electronic components.
Systems were simple but less efficient.

## Slide 23: Component evolution and innovation
1990s
Introduction of electronic controls: basic PCBs, electronic ignition, simple digital displays. Greater efficiency but increased complexity for servicing.
2000s
Advanced modulation: fully electronic systems, sophisticated diagnostics, higher efficiency requirements following UK Building Regulations changes.

## Slide 24: Component evolution and innovation
2010s
Smart controls integration: internet connectivity, remote diagnostics, weather compensation, OpenTherm protocols becoming standard in UK installations.
2020s+
Hydrogen-ready components: developing technology for future fuel transition, hybrid systems combining gas with renewable technologies, AI-enhanced controls.

## Slide 25: Component evolution and innovation
This evolution has significant implications for UK gas engineers:
Increasing technical knowledge requirements.
Greater emphasis on electrical safety and troubleshooting.
Need for continuous professional development.
Adaptation to new technologies and control systems.
The Gas Safe Register now places greater emphasis on electronic control knowledge in ACS assessments, reflecting this industry shift.

## Slide 26: Questions and clarifications
Let's take some time to address any questions you have about today's content.
In particular, consider:
Which components did you find most difficult to understand?
Are there specific appliance types you'd like to explore in more detail?
Do you have experience with component failures that you'd like to discuss?
Are there any areas where UK regulations regarding components seem unclear?

## Slide 27: Questions and clarifications
Remember that understanding gas components is fundamental to your Level 3 Gas Engineering qualification and your future career as a Gas Safe registered engineer.
You're encouraged to sketch systems or components if this helps explain your questions or observations.

## Slide 28: Questions and clarifications
Resources
Additional resources available to support your learning:
Gas Safe Technical Bulletins
Manufacturer training videos
IGEM technical guidance
BSI standards.
For assessment purposes, you should be able to identify components, explain their function, and describe appropriate selection criteria in line with UK gas safety regulations.

## Slide 29: Summary
You should now be able to:
Identify a range of key components used in domestic gas appliances.
Describe their general purpose in gas systems.
Classify appliances based on fuel and system type.
Interpret manufacturer guidance when selecting components.
You might also be able to:
Evaluate the consequences of selecting an unsuitable component.
Link component operation to system behaviour and safety status (AR/ID).

## Slide 30
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.