## Slide 1
Occupational Specialism: Gas Engineering
K1.6 Types of Components and Their Suitability for different appliances and types of systems
PowerPoint 1.6d: Sensor and logic components – thermistors and PCBs

## Slide 2: Starter
Question:
If the boiler was a body, which part would be the brain?
Which would be the nerves?

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe the role of thermistors and PCBs in appliance control.
Identify how these components link to modulation and feedback.
Explain how sensors help appliances respond to demand and faults.
You might also be able to:
Interpret faults caused by sensor or PCB failure.
Analyse feedback loops in gas systems.

## Slide 4: The brain and the nerves of gas appliances
Much like the human body, gas appliances rely on a complex network of components that must work together seamlessly.
Thermistors act as the sensory nerves, gathering information about temperature changes.
The PCB functions as the brain, processing this information and making decisions.
Other components like fans (lungs) and valves (heart) respond to these commands to maintain optimal operation.

## Slide 5: Thermistors: the sensory network
What are thermistors?
NTC thermistors (Negative Temperature Coefficient) are temperature-sensitive resistors commonly used as sensors in gas appliances.
Their key characteristic is that their electrical resistance changes predictably with temperature.

## Slide 6: Thermistors: the sensory network
NTC Thermistor behaviour:
As temperature increases, resistance decreases.
As temperature decreases, resistance increases.

## Slide 7: Thermistors: the sensory network
Common applications in gas appliances:
Flow temperature monitoring
Return temperature monitoring
Cylinder sensors (in system boilers)
Boiler limit sensors (safety functions)
Flue gas temperature monitoring.

## Slide 8: Thermistors: the sensory network
A typical NTC thermistor used in boiler applications.
These compact components are usually clipped or strapped to pipework and connected to the PCB via insulated wires.
Their simple construction belies their critical importance in the safe and efficient operation of gas appliances.
Thermistors are relatively inexpensive components, but their failure can render an entire system inoperable, highlighting their crucial role in modern gas appliances.

## Slide 9: How thermistors work: the temperature-resistance relationship
The NTC principle
Thermistors operate on a fundamental principle: as temperature changes, their electrical resistance changes in a predictable pattern. For NTC (Negative Temperature Coefficient) thermistors:
The relationship between temperature and resistance follows an inverse exponential curve, not a linear pattern. This means small temperature changes at lower temperatures produce larger resistance changes than the same temperature change at higher temperatures.

## Slide 10: How thermistors work: the temperature-resistance relationship
This property allows for greater sensitivity in detecting small temperature variations, particularly in the operating range of most domestic heating systems (20-80°C).
The PCB monitors these resistance changes and uses them to determine the current temperature at the sensor location. It then uses this information to make decisions about appliance operation, such as modulating the gas valve or activating the pump.

## Slide 11: Thermistor circuit in a typical boiler system
The thermistor is securely clipped to the water pipe, monitoring the temperature of the water flowing through.
The wires connect directly to the PCB, which constantly analyses the resistance values to determine the current water temperature.

## Slide 12: Thermistor circuit in a typical boiler system
Temperature change
Water temperature changes in the pipe.
Resistance change
Thermistor resistance increases or decreases in response.
Signal processing
PCB detects the resistance change and calculates temperature.
System response
PCB adjusts gas valve, pump or fan operation accordingly.

## Slide 13: Thermistor circuit in a typical boiler system
This continuous feedback loop allows the boiler to maintain precise temperature control, ensuring comfort for the end user while maximising efficiency and component longevity.
The positioning of thermistors is critical for accurate temperature sensing and proper system response.

## Slide 14: Printed Circuit Board (PCB): the system's brain
PCB functions and capabilities
The PCB is the central processing unit of a modern gas appliance, responsible for coordinating all operations and ensuring safe, efficient performance.
It receives input from multiple sensors, processes this information according to programmed parameters, and controls the operation of various components.

## Slide 15: Printed Circuit Board (PCB): the system's brain
Key control functions:
Ignition sequence timing and safety checks
Fan speed control and pre/post purge cycles
Pump operation and anti-seize protection
Burner modulation for optimal efficiency
System protection from overheating or freezing
Fault detection, recording and display.

## Slide 16: Printed Circuit Board (PCB): the system's brain
A typical PCB found in a modern condensing boiler. Note the various components including:
Microprocessor (the actual "brain")
Relay switches for controlling high-current components
Fuses and surge protection circuitry
Terminal blocks for sensor and component connections
Memory storage for settings and fault codes
Interface connections for displays and controls.

## Slide 17: The Feedback Loop: how gas appliances 'think'
Demand signal
Thermostat or user interface requests heat.
Temperature sensing
Flow thermistor detects current water temperature (low reading = high resistance).
PCB processing
PCB analyses readings and initiates appropriate action sequence.

## Slide 18: The Feedback Loop: how gas appliances 'think'
Component activation
PCB activates fan, opens gas valve, triggers ignition.
Heat generation
Burner ignites and transfers heat to water.
Temperature rise
Water temperature increases, causing thermistor resistance to decrease.

## Slide 19: The Feedback Loop: how gas appliances 'think'
This feedback loop operates continuously during appliance operation.
As the water temperature approaches the setpoint, the PCB will begin to modulate the burner output downward.
If the temperature exceeds the setpoint, the burner may cycle off completely until the temperature drops again.

## Slide 20: The Feedback Loop: how gas appliances 'think'
Modern boilers use proportional control algorithms that consider both the current temperature and the rate of change to provide smoother operation and better temperature stability than older on/off systems.
This constant adjustment based on sensor feedback is what enables high-efficiency operation in contemporary gas appliances.

## Slide 21: Common sensor faults and their effects
Component | Fault type | Symptoms | System response
Flow thermistor | Open circuit | No resistance reading | Boiler lockout with sensor fault code
Flow thermistor | Short circuit | Zero resistance | Boiler lockout with sensor fault code
Return sensor | Degraded/slow response | Inaccurate readings | Poor modulation, cycling, inefficiency
Overheat stat | Tripped | Open circuit on safety loop | Lockout requiring manual reset
PCB | Component failure | No logic or erratic behaviour | Appliance inoperative or unsafe operation
PCB | Relay failure | Component stuck on/off | Fan or pump running permanently or not at all

## Slide 22: Common sensor faults and their effects
When diagnosing sensor-related issues, always test sensors with a multimeter and compare to the manufacturer's installation manual (MI) resistance chart. Remember that a faulty sensor can produce symptoms similar to other component failures, so methodical testing is essential.
PCB faults can be particularly challenging to diagnose as they may cause intermittent issues or unusual behaviour that doesn't follow typical fault patterns. Always check for visible damage such as burnt components, bulging capacitors, or corrosion before replacing a PCB.

## Slide 23: Testing thermistors: resistance measurement
Resistance testing procedure
Isolate the appliance electrically.
Disconnect the thermistor from the PCB.
Set the multimeter to the resistance (Ohms) function.
Connect meter probes to thermistor terminals.
Record the resistance value.
Measure the actual water temperature near the sensor.
Compare the reading with the manufacturer's data.

## Slide 24: Testing thermistors: resistance measurement
Example scenario
An infrared thermometer measures flow temperature at approximately 600C. According to the manufacturer's data, the expected resistance at this temperature should be approximately 3.2kΩ.
If your multimeter shows 10kΩ, this indicates the sensor is not responding correctly to temperature changes and is likely faulty.

## Slide 25: Testing thermistors: resistance measurement
Always ensure the appliance is electrically isolated before disconnecting any components.
Thermistors typically operate on low voltage, but other nearby components may carry mains voltage.
Remember that thermistor resistance values can vary between manufacturers and even between different models from the same manufacturer.
Always refer to the specific appliance's technical documentation for the correct resistance values.

## Slide 26: Testing thermistors: resistance measurement
Some modern systems allow diagnostic access to sensor readings directly through the user interface or service menu, which can help identify discrepancies between what the PCB is reading and actual conditions.

## Slide 27: PCB fault indicators: recognising logic issues
Visual indicators
No LED illumination or display function
Flickering or erratic display screen
Error codes related to communication failures
Visible damage: burnt components, bulging capacitors
Corrosion or water damage on the board surface.

## Slide 28: PCB fault indicators: recognising logic issues
Operational symptoms
Fan or pump running permanently without heat demand
Components not activating when they should
Clicking relays but no ignition sequence
Random cycling or shutdown without fault codes
Multiple unrelated fault codes occurring simultaneously.

## Slide 29: PCB fault indicators: recognising logic issues
Testing Approaches
Measure supply voltage to PCB (typically 230V)
Check output voltages to components (fans, pumps)
Test continuity of fuses and safety circuits
Inspect board for visible damage or overheating
Reset power completely (including batteries if present).

## Slide 30: PCB fault indicators: recognising logic issues
PCB faults often require replacement of the entire board rather than repair of individual components.
When ordering a replacement PCB, always ensure you have the exact model and revision number, as seemingly identical boards may have different firmware or component configurations.
Some manufacturers now offer diagnostic interfaces that connect to laptops or specialised tools, allowing more detailed analysis of PCB function and communication with components.

## Slide 31: Scenario task: Aadil's cold tap problem
Aadil reports that his combi boiler runs when hot water is demanded, but keeps cycling on and off.
Additionally, the heating system is slow to warm up, taking over an hour to reach a comfortable temperature.
In pairs:
What sensor might be involved?
Could the PCB be misreading the temperature?
How would you test the theory?

## Slide 32: Key learning points
Thermistor function - NTC thermistors decrease resistance as temperature increases, providing temperature feedback to the PCB.
PCB processing - The PCB processes sensor inputs and controls component operation according to programmed parameters.
Feedback loops - Continuous monitoring and adjustment create a feedback loop that maintains optimal operation.
Diagnostic techniques - Resistance testing of thermistors and systematic troubleshooting of PCBs are essential diagnostic skills.
Safety implications - Sensor and PCB failures can have serious safety implications if not properly identified and addressed.

## Slide 33: Summary
You should now be able to:
Describe the role of thermistors and PCBs in appliance control.
Identify how these components link to modulation and feedback.
Explain how sensors help appliances respond to demand and faults.
You might also be able to:
Interpret faults caused by sensor or PCB failure.
Analyse feedback loops in gas systems.

## Slide 34
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.