## Slide 1
Occupational Specialism: Gas Engineering
K1.6 Types of components and their suitability for different appliances and types of systems
PowerPoint 1.6g: System suitability, GIUSP classification and troubleshooting

## Slide 2: Starter
Scenario: The strange smell
A customer has reported an unusual odour and a flickering orange flame after having their boiler repaired recently. Upon arrival at the property, you notice a visible gap in the flue joint.
Which three specific components would you prioritise checking in this scenario?
How would you classify this situation according to GIUSP classifications (AR/ID)?
What immediate actions would you take to ensure safety?

## Slide 3: Objectives
By the end of this session, you should be able to:
Determine if a component is suitable for a system or appliance.
Apply GIUSP to classify unsafe situations (AR/ID).
Troubleshoot typical component-based faults.
Use MI and system data to assess compatibility.
You might also be able to:
Justify your fault classification with risk-based reasoning.
Recommend correct remedial actions.

## Slide 4: What is system suitability?
System suitability refers to the comprehensive process of ensuring that every component installed in a gas system is appropriate for its intended purpose and complies with all relevant standards and regulations.

## Slide 5: What is system suitability?
Key suitability factors
The right component for the specific appliance (manufacturer approved).
Compatible with the correct gas type (Natural Gas or LPG).
Designed for the appropriate pressure and flow rate requirements.
Suitable for the installed flue configuration and ventilation setup.
Compliant with current British Standards and industry regulations.
Installed according to the manufacturer's specific instructions.
Remember to reference and follow Manufacturer's Instructions (MIs), appliance data badges, and relevant British Standards for every installation and maintenance operation.

## Slide 6: What is system suitability?
Potential consequences of unsuitable components
Using inappropriate components can lead to:
Dangerous combustion issues including carbon monoxide production.
Reduced efficiency and increased operating costs.
Premature component failure and system damage.
Invalidation of appliance warranty and insurance.
Legal liability for the installing engineer.
Non-compliance with Gas Safety (Installation and Use) Regulations.

## Slide 7: What is system suitability?
Remember that Manufacturer's Instructions (MIs), appliance data badges, and relevant British Standards must be referenced and followed for every installation and maintenance operation.
As registered gas engineers, ensuring system suitability is a fundamental professional responsibility that directly impacts customer safety.

## Slide 8: Component matching recap
Orifice Size Difference (10 -15%)
LPG burner jets typically have 10-15% smaller orifice sizes compared to natural gas equivalents due to higher calorific value.
NG Working Pressure (28 mbar)
Standard working pressure for natural gas appliances in UK installations.
LPG Working Pressure (37 mbar)
Standard working pressure for propane (LPG) appliances in UK installations.

## Slide 9: Component matching recap
Component | Natural Gas Appliance | LPG Appliance
Burner jet | Larger orifice diameter | Smaller orifice diameter
Gas valve | Lower pressure setting | Higher pressure setting
Flame supervision device | Same basic function | Same basic function
Fan/Air pressure switch | Must suit flue resistance | Must suit products of combustion pressure

## Slide 10: Critical consequences of incorrect component selection
Installing the wrong component can lead to several serious issues:
Combustion problems: Incorrect air/gas ratio leading to sooting, carbon monoxide production, and unsafe operation.
System damage: Overpressure, overheating, or premature component failure.
Safety device malfunction: Flame supervision or pressure switch failures that compromise safety interlocks.
Efficiency reduction: Poor performance and increased fuel consumption.

## Slide 11: GIUSP Overview – IGEM/G/11
The Gas Industry Unsafe Situations Procedure (GIUSP) provides a standardised framework for identifying, classifying and responding to unsafe gas installations.
It is published as IGEM/G/11 and is mandatory guidance for all Gas Safe registered engineers in the UK.

## Slide 12: GIUSP Overview – IGEM/G/11
AR (At Risk): A situation that presents a potential danger to life or property if the gas installation continues to be used. Engineer action: Turn off the appliance, attach warning label, and advise customer not to use until repaired. | ID (Immediately Dangerous): A situation that presents an immediate danger to life or property if the gas installation continues to be used. Engineer action: Disconnect and seal the gas supply, attach a warning label, and issue a prohibition notice. | NCS (Not to Current Standards): An installation that does not comply with current standards but is not considered unsafe. Engineer action: Note the non-compliance and inform the customer of the situation. No longer used but still relevant
Unsafe situations are classified into two distinct categories:

## Slide 13: GIUSP Overview – IGEM/G/11
Documentation requirements
For all unsafe situations, engineers must:
Complete the appropriate warning/advisory notice.
Explain the classification and required actions to the responsible person.
Record details in the engineer's own work records.
Report ID situations to the Gas Safe Register when required.
Maintain detailed evidence of the unsafe condition (photographs where possible).

## Slide 14: Faults and their GIUSP classifications
Fault Component | Issue | Classification | Rationale
Air Pressure Switch | No activation when fan runs | ID | Combustion products not being safely removed
Burner | Yellow flame/sooting | AR or ID | Incomplete combustion, potential CO production
Flame Supervision Device | Missing on hob burner | ID | Gas flow without flame detection creates explosion risk
Thermistor | Incorrect readings causing poor modulation | AR | Potential overheat condition, inefficient operation
Multiblock Valve | Bypassed safety function | ID | No flame control, immediate safety risk
Flue Terminal | Incorrect location near openable window | AR or ID | Products of combustion may enter building
Gas Meter | Leaking connection | ID | Gas escape presents immediate danger

## Slide 15: Faults and their GIUSP classifications
Classification depends on severity - factors include:
CO readings in the atmosphere or flue gas analysis.
Evidence of distress or deterioration of the appliance.
Risk to vulnerable occupants (elderly, children, etc.).
Appliance location and ventilation provisions.

## Slide 16: Faults and their GIUSP classifications
When classifying faults, engineers must:
Refer to appliance Manufacturer's Instructions for specific guidance.
Consult IGEM/G/11 for classification criteria.
Apply professional judgement based on evidence and risk assessment.
Document findings thoroughly with appropriate evidence.
Remember that the safety of occupants is always the primary concern. When in doubt about a classification, err on the side of caution and apply the more severe category.

## Slide 17: Fan system troubleshooting: Call for heat
Verify thermostat demand is present:
Check voltage at controller terminals.
Confirm programmer settings.
Test continuity through external controls.

## Slide 18: Fan system troubleshooting: Fan operation
Confirm fan activates when demand is present:
Listen for fan motor.
Check voltage at fan terminals.
Test fan windings for continuity.
Inspect fan impeller for damage/obstruction.

## Slide 19: Fan system troubleshooting: APS activation
Verify Air Pressure Switch (APS) closes:
Check for switch continuity when the fan is running.
Inspect pressure tubes for blockages/splits.
Test switch operation with an external manometer.
Verify correct pressure differential.

## Slide 20: Fan system troubleshooting: PCB sequence
Confirm the ignition sequence proceeds:
Check PCB receives APS signal.
Verify the gas valve energises.
Confirm spark generation.
Check flame detection signal.

## Slide 21: Fan system troubleshooting: Classification and action
If troubleshooting identifies specific faults:
Fan not operating: Classify as AR if cold appliance, ID if signs of spillage.
APS stuck closed: ID - bypassed safety device.
APS not closing when fan runs: ID - flue blockage or fan issue preventing safe evacuation of combustion products.
Pressure tube issues: ID - compromised safety circuit.
Develop similar systematic troubleshooting flowcharts for other common systems such as FSD faults, gas valve issues, and ignition sequence problems to build your diagnostic skills.

## Slide 22: Fault diagnosis: Essential documentation
Manufacturer's Instructions (MI): The definitive source for component specifications, fault codes, and troubleshooting procedures.
Appliance data badge: Contains critical information on gas type, input rating, and serial numbers.
GIUSP / IGEM G/11: Provides classification guidance for unsafe situations.
Wiring diagrams: Essential for electrical fault finding.
Service history: Previous issues may indicate recurring problems.
Gas Safe technical bulletins: Updated guidance on specific issues.

## Slide 23: Fault diagnosis: Diagnostic equipment
Multimeter: For measuring resistance, voltage, and continuity.
Manometer: For gas pressure and differential pressure testing.
Flue gas analyser: For combustion performance assessment.
Leak detection fluid: For identifying gas escapes.
Inspection mirrors and torches: For visual inspection of hard-to-reach areas.
Temperature probes: For verifying correct operating temperatures.
Digital camera: For documenting fault conditions.

## Slide 24: Fault diagnosis: Professional judgement
When diagnosing faults, your professional judgement must be:
Evidence-based and systematic.
Documented thoroughly with test results.
Consistent with manufacturer guidance.
Applied with safety as the paramount concern.
Develop a methodical approach to fault diagnosis that combines technical knowledge with systematic testing procedures.

## Slide 25: Scenario task: Ash changes a component
The scenario
Ash, a heating engineer, has replaced a thermistor on a combi boiler.
Instead of using the manufacturer's approved part, they used a similar thermistor from another make of boiler that they had in their van.
After the replacement, the boiler now overheats and cuts out on high temperature lockout.

## Slide 26: Scenario task: Ash changes a component
Discussion questions
What technical issue has likely occurred with the replacement thermistor?
Which specific document would you check to identify the correct replacement part?
What GIUSP classification would apply to this situation?
What remedial actions would be required to resolve the issue?
What advice should you give to the customer about this situation?

## Slide 27: Scenario task: Ash changes a component
Technical analysis
Thermistors are precision components with specific resistance values that vary with temperature. Using an incorrect thermistor can result in:
Inaccurate temperature readings being sent to the PCB.
Improper modulation of the burner.
Failure to detect actual overheating conditions.
False overheating signals when temperatures are normal.
Unpredictable appliance behaviour and cycling.

## Slide 28: Formative quiz: GIUSP and suitability
Which GIUSP classification applies to each of the following scenarios?
Pressure switch issue - The fan in a room-sealed boiler runs normally, but the air pressure switch fails to trigger, preventing ignition sequence.
Missing FSD - A cooker burner operates without a functioning flame supervision device, allowing gas flow without flame detection.
Valve malfunction - A multiblock valve on a commercial heating system has been found with the safety interlock mechanisms bypassed.
Incorrect injector - An LPG fire has been fitted with a natural gas injector, causing a large, lazy yellow flame.

## Slide 29: Formative quiz – GIUSP and suitability
Which GIUSP classification applies to each of the following scenarios?
1. Pressure switch issue
The fan in a room-sealed boiler runs normally, but the air pressure switch fails to trigger, preventing ignition sequence.
Classification: ID (Immediately Dangerous)
Rationale: Without APS confirmation, there's no guarantee that combustion products will be safely evacuated, creating immediate risk of carbon monoxide poisoning.

## Slide 30: Formative quiz – GIUSP and suitability
Which GIUSP classification applies to each of the following scenarios?
2. Missing FSD
A cooker burner operates without a functioning flame supervision device, allowing gas flow without flame detection.
Classification: ID (Immediately Dangerous)
Rationale: Gas could flow without ignition, creating immediate explosion risk. GSIUR specifically requires FSD on all burners except those continuously supervised.

## Slide 31: Formative quiz – GIUSP and suitability
Which GIUSP classification applies to each of the following scenarios?
3. Valve malfunction
A multiblock valve on a commercial heating system has been found with the safety interlock mechanisms bypassed.
Classification: ID (Immediately Dangerous)
Rationale: This deliberate defeat of safety devices creates immediate risk of explosion or carbon monoxide production with no automatic shutdown protection.

## Slide 32: Formative quiz – GIUSP and suitability
Which GIUSP classification applies to each of the following scenarios?
4. Incorrect injector
An LPG fire has been fitted with a natural gas injector, causing a large, lazy yellow flame.
Classification: AR or ID (depending on CO readings)
Rationale: Incomplete combustion creates CO risk. If CO readings exceed safety thresholds in the room or flue gases, classify as ID; otherwise AR.

## Slide 33: Key takeaways
Always refer to manufacturer's instructions before replacing any component.
Correct component selection is critical for safe and efficient operation.
GIUSP classifications must be applied consistently and documented thoroughly.
Systematic troubleshooting improves efficiency and accuracy in fault diagnosis.
Professional judgement must be backed by technical evidence and measurements.

## Slide 34: Summary
You should now be able to:
Determine if a component is suitable for a system or appliance.
Apply GIUSP to classify unsafe situations (AR/ID).
Troubleshoot typical component-based faults.
Use MI and system data to assess compatibility.
You might also be able to:
Justify your fault classification with risk-based reasoning.
Recommend correct remedial actions.

## Slide 35
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.