## Slide 1
Occupational Specialism: Gas Engineering
K1.7 How components operate within a system/appliance and integrate to enable the system to operate effectively
PowerPoint 1.7a: Component functions and system integration

## Slide 2: Starter
A boiler’s fan fails to run during ignition. What happens next?
Discuss in pairs:
Will the burner light?
What will the air pressure switch do?
What is the role of the PCB in this situation?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify key gas appliance components and their roles.
Describe how each component supports ignition, combustion, or temperature control.
Explain how components interact with each other in a control sequence.
Recognise the importance of system integration for safe operation.

## Slide 4: Fan components in gas appliances
Primary purpose
Creates controlled airflow essential for efficient combustion.
Ensures proper removal of waste gases in room-sealed appliances.
Maintains positive pressure differential between combustion chamber and flue.
Prevents products of combustion from entering living spaces.

## Slide 5: Fan components in gas appliances
System integration
Must run and prove airflow before burner ignition sequence can proceed.
Directly controlled by PCB based on heat demand signals.
Provides feedback via Air Pressure Switch (APS) to confirm operation.
May operate at variable speeds in high-efficiency modulating appliances.
Often integrated with venturi devices for precise air-gas mixture control.

## Slide 6: Fan components in gas appliances
Common applications
Found in combination boilers, system boilers, modern water heaters, and any room-sealed appliance requiring forced draught for combustion products.

## Slide 7: Air/gas ratio control valve
Structure and design
Modern air/gas ratio valves incorporate precision components including diaphragms, springs, and adjustment mechanisms that work together to maintain the optimal combustion ratio across varying operational demands.

## Slide 8: Air/gas ratio control valve
Purpose and function
The device is able to maintain the correct air/gas ratio of 10:1 while modulating the burner for different outputs.
It responds dynamically to changes in demand, adjusting gas flow proportionally to air supply to maintain efficiency and prevent incomplete combustion.

## Slide 9: Air/gas ratio control valve
Safety implications
Proper ratio control is critical for preventing the production of carbon monoxide.
If the ratio becomes too rich (excess gas) or if combustion air is restricted, CO levels can rise to dangerous levels.
Modern valves include redundant safety features to prevent hazardous conditions.

## Slide 10: Air/gas ratio control valve
System integration
In modern appliances, the ratio valve is modulated by the PCB based on inputs from multiple sensors including thermistors, fan speed, and sometimes flue gas analysis.
This integration allows for precise control across the modulation range, optimising efficiency while maintaining safe operation even at minimum input rates.
Found primarily in high-efficiency condensing boilers, some advanced fires, and commercial space heating systems where emissions control and efficiency are paramount.

## Slide 11: Thermistors (NTCs)
Purpose and operation
Thermistors are temperature-sensitive resistors, typically of the Negative Temperature Coefficient (NTC) type, meaning their resistance decreases as temperature increases.
This predictable relationship allows the PCB to calculate precise temperature readings.

## Slide 12: Thermistors (NTCs)
Flow thermistor
Measures the temperature of water leaving the heat exchanger. Critical for controlling burner modulation and preventing overheating. Typically operates in a range of 35-85°C.
Return thermistor
Monitors water temperature returning to the boiler. Used to calculate ΔT (temperature differential), which helps determine heat transfer efficiency and identify potential issues like blockages.

## Slide 13: Thermistors (NTCs)
DHW thermistor
Measures domestic hot water temperature to ensure consistent output and prevent scalding.
Often regulates temperature to 42-65°C, depending on user settings.

## Slide 14: Thermistors (NTCs)
System integration
Thermistors provide continuous feedback to the PCB, which uses these readings to:
Modulate burner output to match heat demand precisely.
Adjust pump speed for optimal flow rates and efficiency.
Trigger safety cut-off if overheat conditions are detected (typically at 90-95°C).
Calculate flow rates in some appliances without flow sensors.

## Slide 15: Thermistors (NTCs)
Determine when frost protection mode should activate (usually below 5°C).
Monitor heat exchanger conditions to prevent thermal stress.
The resistance values of NTC thermistors at various temperatures are critical diagnostic information.
For example, a typical 10K NTC thermistor might read 27-28kΩ at 0°C, 10kΩ at 25°C, and 1kΩ at 100°C.
Deviation from expected values can indicate sensor failure or calibration issues.

## Slide 16: Printed Circuit Board (PCB)
The control centre of modern gas appliances
The PCB represents the central nervous system of contemporary gas appliances, incorporating microprocessors, memory, and I/O circuitry to coordinate all operational aspects.
Modern PCBs have evolved from simple relay controllers to sophisticated computers capable of complex algorithms and fault analysis.

## Slide 17: Printed Circuit Board (PCB)
Input signals processed
Temperature readings from multiple thermistors (flow, return, DHW).
Air pressure switch confirmation of fan operation.
Flame rectification signal (typically 1-5μA DC current).
User interface selections and temperature setpoints.
External controls (room thermostats, OpenTherm devices).
Water pressure transducer readings (typically 0.5-3.5 bar).
Flow switches or Hall effect sensors for DHW detection.

## Slide 18: Printed Circuit Board (PCB)
Output control functions
Ignition sequence timing and spark generation.
Fan speed control (often using PWM signals).
Gas valve modulation for precise heat output.
Pump speed control for efficient water circulation.
Diverter valve positioning for mode selection.
Safety shutdown coordination and lockout procedures.
Diagnostic LED or display interface communication.

## Slide 19: Printed Circuit Board (PCB)
Diagnostic capabilities
Modern PCBs store fault codes and operational history, allowing engineers to diagnose intermittent issues.
They can detect subtle faults like flame loss, ignition failure, circulation problems, and sensor discrepancies, often before they become critical failures.

## Slide 20: Printed Circuit Board (PCB)
Diagnostic capabilities
Some manufacturers now include remote diagnostic capabilities via internet connections, allowing parameter adjustments without physical access.
The PCB represents approximately 25-40% of the total cost of a modern gas appliance, making proper diagnosis of PCB issues versus peripheral component failures crucial for cost-effective repairs.

## Slide 21: Multi-Functional Control Valve (MFCV)
Integrated functions
The MFCV combines multiple gas control functions into a single compact unit, reducing potential leak points and simplifying appliance design.

## Slide 22: Multi-Functional Control Valve (MFCV)
These components work in harmony to provide safe, controlled gas delivery:
Manual isolation valve: Allows physical shutoff of gas supply during service or emergency.
Solenoid valve(s): Electrically controlled valves that open/close automatically based on PCB commands.
Pressure regulator: Maintains consistent gas pressure regardless of supply fluctuations.

## Slide 23: Multi-Functional Control Valve (MFCV)
These components work in harmony to provide safe, controlled gas delivery:
Test points: Allows measurement of inlet, outlet, and sometimes burner pressure.
Throttle adjustment: Permits calibration of maximum and minimum gas rates.
Venturi connection: In some models, interfaces with the air-gas mixing system.

## Slide 24: Multi-Functional Control Valve (MFCV)
System integration
The MFCV is controlled by the PCB and operates in conjunction with other safety systems:
Will not open unless proper ignition sequence is confirmed.
Linked to thermocouple/flame sensor to ensure continued combustion.
Modern valves include redundant solenoids for Class B safety compliance.
Often incorporates modulation capabilities via stepper motors or proportional solenoids.

## Slide 25: Multi-Functional Control Valve (MFCV)
Operating voltages vary by manufacturer, with 24V DC common for residential appliances and 230V AC for some commercial systems.
Current draw is typically 0.3-0.5A during operation, with higher inrush currents at activation.

## Slide 26: Air Pressure Switch (APS)
Construction and operation
The APS consists of a diaphragm-operated switch with positive and negative pressure ports.
When sufficient pressure differential is detected (typically 10-25 Pa depending on appliance), the diaphragm moves to close an electrical contact, sending a signal to the PCB that proper airflow has been established.

## Slide 27: Air Pressure Switch (APS)
Installation and connection
The APS is positioned between the fan and flue system, and silicone tubes connect to sampling points that measure the pressure differential.
Positive pressure is typically measured at the fan outlet, while negative pressure may be measured at the venturi or combustion chamber.

## Slide 28: Air Pressure Switch (APS)
Testing and diagnostics
Engineers can test APS operation using a digital manometer to verify switching pressures.
A properly functioning switch should close at or above the rated pressure differential and open when pressure drops below threshold.
Modern digital analysers can also simulate APS operation for diagnostic purposes.

## Slide 29: Air Pressure Switch (APS)
Critical safety function
The APS serves as a vital safety interlock in the ignition sequence:
Prevents burner ignition if the fan fails to create sufficient draught.
Detects flue blockages that could lead to dangerous combustion product spillage.
Confirms proper mechanical operation of the fan before gas is introduced.
In some systems, it helps verify proper venturi operation for air-gas mixing.

## Slide 30: Air Pressure Switch (APS)
BS 5440-1 requires that room-sealed appliances include provisions to prevent operation if the flue becomes obstructed.
The APS is the primary method of meeting this requirement in fan-assisted systems.
Failure of the APS to prove is one of the most common causes of lockout in modern boilers, often indicating flue blockage, condensate issues, or fan problems.

## Slide 31: Flame Supervision Device (FSD)
Purpose and critical safety role
The Flame Supervision Device represents one of the most crucial safety components in any gas appliance, designed to confirm the presence of a flame and prevent the dangerous accumulation of unburned gas in the event of ignition failure or flame loss during operation.

## Slide 32: Flame Supervision Device (FSD)
Types of flame detection systems: Thermocouple
The most basic form of FSD, consisting of a metal probe positioned in the flame.
Heat generates a small thermoelectric voltage (typically 25-30mV) that energises a holding coil in the gas valve.
If flame is lost, the thermocouple cools and voltage drops, allowing the valve to close automatically. Response time: 30-60 seconds.

## Slide 33: Flame Supervision Device (FSD)
Types of flame detection systems: Thermopile
Similar to a thermocouple but consisting of multiple junctions in series to generate higher voltage (250-750mV).
This allows operation of larger valves or electronic systems without external power.
Commonly used in decorative fires and some water heaters.

## Slide 34: Flame Supervision Device (FSD)
Types of flame detection systems: Flame rectification
Modern electronic systems use a probe positioned in the flame to detect the rectifying effect of flame on AC current.
The flame acts as a diode, creating a small DC current (1-5μA) that is detected by the PCB.
Response time: 1-2 seconds, allowing rapid shutdown if flame is lost.

## Slide 35: Flame Supervision Device (FSD)
Types of flame detection systems: Optical sensors
Used in some commercial applications, these detect the UV or IR radiation produced by the flame.
Highly sensitive but less common in domestic appliances due to cost and complexity.

## Slide 36: Flame Supervision Device (FSD)
System integration
The FSD integrates with other components to ensure safe operation:
In basic appliances, directly controls gas valve without electronic intervention.
In modern systems, sends signal to PCB which then controls the gas valve.
May trigger immediate lockout or attempt re-ignition depending on appliance design.
Flame proving window typically 5-10 seconds during startup sequence.
Must detect flame loss within 1 second in high-efficiency appliances.

## Slide 37: Flame Supervision Device (FSD)
Common fault patterns
FSD failures manifest in predictable ways that aid diagnosis:
Appliance lights but immediately shuts down: Poor flame signal or damaged sensor.
Intermittent operation: Weak flame signal or marginal thermocouple.
Delayed shutdown after flame loss: Slow response time or carbon deposits.
Failure to light with spark visible: FSD preventing gas valve operation.
According to Gas Safe statistics, FSD failures contribute to approximately 18% of dangerous gas appliance incidents, highlighting their critical safety importance.

## Slide 38: Component sequence, combi boiler DHW operation
Demand detection
When a hot water tap opens, water flows through the DHW flow sensor (typically Hall effect or impeller type), generating a signal to the PCB indicating demand.
Flow rate must typically exceed 2-3 l/min to trigger operation.

## Slide 39: Component sequence, combi boiler DHW operation
Fan pre-purge
PCB activates the fan to perform a pre-purge cycle (typically 5-10 seconds), clearing any residual combustion products from the heat exchanger.
Fan speed is controlled via PWM signal from the PCB, with initial RPM determined by appliance model.

## Slide 40: Component sequence, combi boiler DHW operation
Air pressure verification
Once the fan reaches operational speed, the APS detects the pressure differential and closes its contacts, sending a confirmation signal to the PCB that proper airflow exists for safe combustion.
Ignition sequence
PCB energises the ignition electrode (typically 15-25kV) while simultaneously opening the gas valve.
This creates a spark across the electrode gap, igniting the air-gas mixture flowing through the burner.

## Slide 41: Component sequence, combi boiler DHW operation
Flame verification
The flame rectification probe detects the flame, sending a DC microamp signal to the PCB.
If no flame is detected within the safety time (typically 5 seconds), the gas valve closes and the appliance attempts reignition or enters lockout.

## Slide 42: Component sequence, combi boiler DHW operation
Temperature monitoring
DHW thermistor continuously monitors water temperature, sending resistance values to the PCB.
These values vary inversely with temperature (e.g., 12kΩ at 20°C, 2kΩ at 60°C), allowing precise temperature calculation.

## Slide 43: Component sequence, combi boiler DHW operation
Output modulation
PCB modulates gas valve and fan speed to maintain target DHW temperature (typically 42-65°C depending on user settings).
Higher flow rates trigger increased gas input to maintain temperature stability.

## Slide 44: Component sequence, combi boiler DHW operation
Shutdown sequence
When the tap closes, flow sensor signals cessation of demand. PCB closes gas valve, continues fan operation for post-purge cycle (typically 5-30 seconds), then returns to standby mode, ready for next demand.

## Slide 45: Component fault analysis: Cause and effect
Fan faults
Symptoms: Boiler fails to ignite, fan error code, unusual fan noise.
Causes: Bearing failure, electrical connection issues, PCB fault, condensate blockback.
Effect on system: APS will not close, preventing ignition sequence from proceeding. PCB typically enters lockout mode after 3-5 attempts. May display fan fault code (e.g., E041 on Worcester, F125 on Vaillant).

## Slide 46: Component fault analysis: Cause and effect
Fan faults
Testing: Measure fan voltage (typically 230V AC or DC PWM signal, depending on model). Check the resistance of windings. Inspect for mechanical obstruction or condensate ingress.

## Slide 47: Component fault analysis: Cause and effect
Thermistor faults
Symptoms: Erratic temperature control, overheating, boiler cycling, sensor fault codes.
Causes: Wire break, corrosion at connections, thermistor element failure, incorrect mounting.
Effect on system: PCB receives incorrect temperature readings, leading to improper modulation. May cause premature burner shutdown or failure to reach target temperature. Safety circuit may trigger lockout if flow temperature appears to exceed limits.

## Slide 48: Component fault analysis: Cause and effect
Testing: Measure resistance at various temperatures and compare to the manufacturer's chart. A typical NTC thermistor should read 10kΩ at 25°C.

## Slide 49: Component fault analysis: Cause and effect
Flame supervision failures
Symptoms: Ignition failure, flame loss during operation, repeated lockouts.
Causes: Dirty flame electrode, incorrect electrode positioning, poor earth connection, damaged electrode insulation.
Effect on system: Intermittent flame detection may cause nuisance shutdowns. Complete failure prevents burner operation. PCB often shows ignition failure or flame loss codes.

## Slide 50: Component fault analysis: Cause and effect
Testing: Inspect electrode for carbon deposits or damage. Measure flame current (typically 1-5μA DC) using microamp meter in series with electrode. Check electrode gap to burner (typically 3-5mm).
Component failures rarely occur in isolation.
A fault in one component often places additional stress on others, potentially leading to cascading failures.
For example, a partially blocked heat exchanger may cause overheating, putting stress on the thermistors, pump, and fan, potentially leading to premature failure of these components.

## Slide 51: Component fault analysis: Cause and effect
According to Gas Safe Register data, approximately 22% of dangerous gas appliance incidents involve component interaction issues rather than single component failures, highlighting the importance of understanding system integration during fault diagnosis.

## Slide 52: Component compatibility and replacements
Manufacturer specifications
Gas appliance components are carefully matched to ensure proper system integration and safe operation.
Manufacturers design components to work together with specific electrical and mechanical characteristics:
PCBs are programmed with parameters specific to the appliance model.
Fan speeds are calibrated to match flue design and burner requirements.
Gas valves are matched to input ratings and control signal types.
Thermistors must have the correct resistance curves for accurate temperature reading.

## Slide 53: Component compatibility and replacements
Replacement considerations
When replacing components, engineers must adhere to strict guidelines to maintain safety and efficiency:
Always use manufacturer-approved replacement parts where specified.
Verify electrical compatibility (voltage, current, signal type).
Check physical fitment and connection types.
Consider software/firmware compatibility with modern PCBs.
After replacement, perform full functional testing of the control sequence.

## Slide 54: Component compatibility and replacements
Legal and safety requirements
The Gas Safety (Installation and Use) Regulations place specific requirements on component replacement:
Regulation 26(5) requires that appliances are maintained in a safe condition.
Using incorrect components may constitute "unsafe work" under Regulation 7.
Components affecting combustion must maintain the appliance within manufacturer specifications.
CE/UKCA marked components should not be modified or adapted.

## Slide 55: Component compatibility and replacements
Using non-approved components can invalidate appliance certification, violate Building Regulations, and potentially invalidate property insurance.
In case of incident, the installing engineer may be held liable for using non-standard parts.
The BS 6798 installation standard specifies that components should be replaced "like for like" unless a manufacturer-approved alternative is specified in technical documentation.

## Slide 56: Advanced component technologies
Smart controls integration
Modern gas appliances increasingly feature connectivity options that allow integration with smart home systems.
OpenTherm, BUS, and wireless protocols enable bidirectional communication between appliances and controls, allowing for weather compensation, load modulation, and remote diagnostics.
These systems can reduce fuel consumption by 15-30% compared to traditional on/off controls.

## Slide 57: Advanced component technologies
Premix combustion systems
Advanced premix systems use precisely controlled air-gas mixtures for optimal combustion efficiency.
Unlike traditional atmospheric burners, premix systems incorporate venturi devices, variable speed fans, and ratio control valves to maintain ideal combustion parameters across the entire modulation range.
This results in NOx emissions below 40mg/kWh, meeting Class 6 requirements.

## Slide 58: Advanced component technologies
Self-diagnostic capabilities
Contemporary appliances incorporate extensive self-diagnostic functions that monitor component performance in real-time.
These systems can detect degradation before complete failure occurs, store operational history, and communicate specific fault information to engineers.
Some manufacturers now offer remote diagnostic capabilities, allowing parameter adjustments without site visits.

## Slide 59: Advanced component technologies
Implications for Gas Engineers
These technological advances require gas engineers to continually update their knowledge and skills:
Technical knowledge requirements
Understanding of electronic control principles and communication protocols.
Familiarity with manufacturer-specific diagnostic software.
Ability to interpret complex fault codes and system parameters.
Knowledge of combustion analysis and adjustment procedures.

## Slide 60: Advanced component technologies
Diagnostic equipment needs
Digital multimeters with microamp measurement capability.
Electronic combustion analysers with CO/CO₂ measurement.
Manufacturer-specific interface tools and software.
Pressure measuring devices with high resolution (0.1 Pa).
According to industry research, approximately 65% of modern gas appliance faults require electronic diagnosis rather than traditional mechanical troubleshooting, highlighting the evolving nature of gas engineering skills.
​

## Slide 61: Key learning point
Session summary
Each gas appliance component has a specific role, from managing gas flow to ensuring safe combustion.
The PCB coordinates their operation with safety interlocks to prevent hazards.
Understanding these connections is key for diagnosing faults, as all parts contribute to the appliance’s safety system.

## Slide 62: Summary
You should now be able to:
Identify key gas appliance components and their roles.
Describe how each component supports ignition, combustion, or temperature control.
Explain how components interact with each other in a control sequence.
Recognise the importance of system integration for safe operation.

## Slide 63
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.