## Slide 1
Occupational Specialism: Gas Engineering
K1.7 How components operate within a system/appliance and integrate to enable the system to operate effectively
PowerPoint 1.7b: Component integration in real appliances

## Slide 2: Starter
Fault scenario: A combi boiler fails to ignite. The fan runs, but no spark occurs. What components should you check in order?
Discussion points
Discuss the likely control chain in this sequence.
What feedback signal is the PCB waiting for?
What tests could confirm the issue?

## Slide 3: Objectives
By the end of this session, you should be able to:
Map components onto real gas appliances.
Explain how components interact during appliance operation.
Interpret simple wiring/functional diagrams from MIs.
Evaluate the effect of a component fault on appliance performance.

## Slide 4: Typical combi boiler – key components
Trigger (DHW or CH demand): Flow sensor or thermostat signals PCB.
Fan operation: Purges combustion chamber.
APS proves: Confirms proper airflow.
Ignition & flame proving: Spark generated, gas valve opens.
Thermistor feedback: Monitors water temperature.
Modulation: Adjusts gas rate to match demand.

## Slide 5: Typical combi boiler – key components
Fan: Provides combustion air and expels flue gases.
Air Pressure Switch (APS): Safety device that confirms proper ventilation.
Gas valve: Controls gas flow to the burner.
Electrode & ignition lead: Generates spark for ignition.

## Slide 6: Typical combi boiler – key components
Flow sensor: Detects water flow for DHW demand.
DHW and CH thermistors: Temperature sensors.
Printed Circuit Board (PCB): Control centre for all operations.
Flame sensing electrode: Confirms flame presence.
Pump: Circulates water through the system.

## Slide 7: Typical combi boiler – key components
The combi boiler is the most complex domestic gas appliance, with the PCB coordinating a precise sequence and monitoring sensor feedback for safe, efficient operation.
During heating, the PCB only advances when the previous stage is confirmed.
For example, the gas valve opens only after the APS verifies airflow, preventing combustion in poor ventilation. This integration of mechanical, electrical, and electronic parts adds safety layers and enables precise temperature and gas control.

## Slide 8: Water heater (Instantaneous)
Key features
No heating circuit – DHW only.
Flow sensor to trigger ignition.
Thermistor for temperature control.
Solenoid valve to modulate gas.
Basic PCB or ignition board.
Flame Supervision Device (FSD) for flame presence.
Can be open flued (Type B) or room-sealed (Type C).

## Slide 9: Water heater (Instantaneous)
Instantaneous water heaters are simpler than combi boilers but still employ sophisticated integration between components.
The primary trigger is almost always water flow, making the flow switch or turbine a critical component in the control chain.
Many modern water heaters feature electronic temperature control, allowing precise regulation of outlet temperature regardless of flow rate or inlet temperature variations.
This is achieved through constant communication between the thermistor and the gas valve modulation system.

## Slide 10: Water heater (Instantaneous)
Tap opens: Water flow begins through the appliance.
Flow switch triggers PCB: Detects water movement, signals for ignition sequence.
Fan starts (if applicable): Begins purge cycle in room-sealed models.
APS proves: Confirms proper ventilation.
Spark + gas: Ignition occurs as gas valve opens.
Flame proven: FSD confirms stable combustion.
Temperature modulation: Thermistor feedback adjusts gas rate.

## Slide 11: Space heater / gas fire
Gas fires represent a simpler component integration compared to boilers, yet they incorporate essential safety features and control mechanisms.
The integration primarily focuses on ensuring safe ignition, maintaining stable combustion, and preventing gas release without flame presence.
In modern room-sealed models, the addition of a fan and air pressure switch creates a more complex control chain similar to boilers, though typically with less sophisticated modulation capabilities.

## Slide 12: Space heater / gas fire
Feature | Description
Ignition | Manual (piezo) or automatic (electronic)
FSD | Thermocouple or Oxygen Depletion Sensor (ODS)
Gas control | Manual or thermostatic
Room sealed/open flued | Affects whether APS and fan are needed
Modulation | Fixed or 2-stage in advanced models

## Slide 13: Space heater / gas fire
Common integration pattern
The ODS sensor monitors oxygen levels in the room.
If levels drop, it causes the thermocouple to cool, which then releases the gas valve and cuts off the supply.
This simple but effective integration protects users from the dangers of carbon monoxide without requiring electronic controls.

## Slide 14: Cookers and hobs
Gas cookers and hobs represent the simplest form of component integration in gas appliances.
They typically lack electronic controls, instead relying on mechanical systems and thermally activated safety devices.
The primary safety integration revolves around the Flame Supervision Device (FSD), which prevents gas flow if no flame is present.
This is particularly important in these Type A (flueless) appliances as they operate directly in the living space without dedicated flue systems.

## Slide 15: Cookers and hobs
Key features
Usually Type A (flueless) appliances.
Require FSDs on all burners (mandatory post-2010).
Ignition systems may be manual or electronic.
No PCB or fan components.
Flame rectification or thermocouple on each burner.

## Slide 16: Cookers and hobs
Key integration
FSD cuts gas if flame fails or is extinguished.
Gas valve is spring-loaded, held open by heat from thermocouple.
No combustion control – relies on user input and built-in safety devices.
Multi-point safety system with individual FSDs for each burner.

## Slide 17: Cookers and hobs
The thermocouple-based safety system demonstrates elegant mechanical engineering - when heated by the flame, it generates a small electrical current (millivolts) that holds an electromagnetic valve open against spring pressure.
If the flame extinguishes, the current stops and the valve closes automatically.

## Slide 18: Wiring and functional schematics
Manufacturer's Instructions (MIs) contain essential wiring diagrams that map the electrical relationships between components.
Understanding these schematics is crucial for effective diagnosis and repair.
Discussion points
What happens if a thermistor fails? The PCB may receive incorrect temperature readings, potentially causing the boiler to shut down, operate continuously, or modulate incorrectly depending on the failure mode (open or short circuit).

## Slide 19: Wiring and functional schematics
What about if the fan fails, but the APS is still working? This is a dangerous scenario - if the APS contacts were to stick closed, the PCB might proceed with ignition despite inadequate ventilation.
This highlights why multiple safety components are integrated into the system.

## Slide 20: Real-world scenario mapping
Scenario
No DHW output. Flow sensor working, but burner does not light.
Confirm flow signal to PCB
Verify the PCB is receiving the demand signal from the flow sensor by checking voltages or using diagnostic tools.
Check fan/APS operation
Confirm the fan runs when DHW flow is detected and the APS contacts close to signal proper airflow.

## Slide 21: Real-world scenario mapping
Look for spark
If missing, test electrode condition, ignition lead continuity, and PCB output voltage.
If spark present
Check gas valve coil resistance and wiring, test flame sensing circuit.
Diagnose root cause
Could be flame sensing failure, gas valve fault, or miswired component.

## Slide 22: Real-world scenario mapping
This scenario demonstrates the importance of understanding component integration when diagnosing faults.
The systematic approach follows the control chain through the appliance, checking each component in sequence to identify where the chain is broken.
By understanding the interdependencies between components, an engineer can efficiently isolate problems without unnecessary disassembly or parts replacement.
This approach is more effective than simply replacing components based on symptoms.

## Slide 23: Real-world scenario mapping
When diagnosing complex issues, it's essential to reference the manufacturer's wiring diagrams and understand how each component should interact within the system.
Testing should follow the logical flow of operations, checking each stage of the sequence until the fault is identified.

## Slide 24: Knowledge check (short answer)
1. Flue gas safety
What component ensures flue gases are being safely expelled before ignition?

## Slide 25: Knowledge check (short answer)
1. Flue gas safety
What component ensures flue gases are being safely expelled before ignition?
The Air Pressure Switch (APS) confirms proper ventilation by detecting the differential pressure created by the fan, ensuring flue gases will be safely expelled before allowing ignition to occur.
This critical safety component prevents combustion in poorly ventilated conditions.

## Slide 26: Knowledge check (short answer)
2. Temperature control
What does a thermistor do in a hot water system?

## Slide 27: Knowledge check (short answer)
2. Temperature control
What does a thermistor do in a hot water system?
A thermistor monitors water temperature by changing its resistance as temperature changes.
This provides continuous feedback to the PCB, allowing precise temperature control through modulation of the gas valve or burner output.
It also provides overheat protection.

## Slide 28: Key takeaways
Understanding component integration is fundamental to effective gas engineering practice.
The knowledge you've gained in this session forms the foundation for advanced skills in commissioning, fault diagnosis, and system optimisation.
Remember that safety systems are designed with multiple layers of protection through component integration.
Always consider how components interact with each other when diagnosing faults or assessing system performance.

## Slide 29: Summary
You should now be able to:
Map components onto real gas appliances.
Explain how components interact during appliance operation.
Interpret simple wiring/functional diagrams from MIs.
Evaluate the effect of a component fault on appliance performance.

## Slide 30
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.