## Slide 1
Occupational Specialism: Gas Engineering
K1.11 Gas and the combustion process
PowerPoint 1.11a: Combustion chemistry – complete vs incomplete

## Slide 2: Starter
Scenario
Georgia's boiler flame has turned yellow, and the casing feels hotter than usual. There's also a strong smell near the flue.
Discuss:
What might be happening inside the combustion chamber?
What causes a flame to burn yellow?
What risks does this pose to the occupant?

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe the process of complete and incomplete combustion.
Explain the chemical by-products of each reaction.
Identify visual and measurable signs of unsafe combustion.
Link combustion conditions to appliance performance and safety.

## Slide 4: What is combustion?
Combustion is a chemical reaction between a fuel and oxygen, releasing heat and light energy.
It is an exothermic oxidation process that forms the basis of all gas appliance operation.
Basic equation (using methane as an example):
This balanced equation shows that one molecule of methane (CH₄) reacts with two molecules of oxygen (O₂) to produce one molecule of carbon dioxide (CO₂), two molecules of water (H₂O), and heat energy.

## Slide 5: What is combustion?
Key requirements:
Adequate oxygen supply (primary and secondary air)
Correct gas/air ratio (stoichiometric mixture)
Ignition source of sufficient temperature
Contained environment with proper ventilation
Appropriate pressure and flow rates
This process occurs in all gas appliances including boilers, water heaters, cookers, fires, and industrial equipment. The efficiency and safety of these appliances depend on achieving proper combustion conditions.

## Slide 6: Complete combustion
Sufficient oxygen
Complete combustion requires the stoichiometric amount of oxygen or slightly more (excess air) to ensure all fuel molecules react fully.
Visual signs
Steady blue flame with well-defined inner and outer cones
No visible soot or yellow colouration
Clean heat exchanger surfaces

## Slide 7: Complete combustion
By-products
Carbon dioxide (CO₂)
Water vapour (H₂O)
Heat energy (enthalpy)
Trace amounts of nitrogen oxides (NOₓ)
Measurable indicators
CO₂ readings of 8-10% in flue gas. CO levels below 20ppm. Flue gas temperature within manufacturer's specifications.

## Slide 8: Complete combustion
Efficiency benefits
Maximum heat transfer
Lower fuel consumption
Reduced maintenance requirements
Extended appliance lifespan
Complete combustion represents the ideal combustion scenario that gas engineers strive to achieve through proper installation, commissioning and maintenance.
It maximises efficiency while minimising safety risks and environmental impact.

## Slide 9: Incomplete combustion
What happens
Incomplete combustion occurs when there is insufficient oxygen available for the fuel to burn completely. This results in partial oxidation of the fuel, producing harmful by-products and reducing efficiency.
Chemical equation (simplified for methane):
Primary causes:
• Blocked air inlets or ventilation • Incorrect gas pressure • Blocked or damaged flue • Incorrectly adjusted burners • Heat exchanger fouling

## Slide 10: Incomplete combustion
By-products
Carbon monoxide (CO) - highly toxic
Soot (carbon particles)
Water vapour (H₂O)
Unburned hydrocarbons
Less heat energy than complete combustion

## Slide 11: Incomplete combustion
Visual signs
Yellow/orange flame instead of blue
Sooting on heat exchanger or around appliance
Excessive condensation
Discoloration of appliance casing
Staining around flue terminal

## Slide 12: Incomplete combustion
DANGER - Carbon monoxide
Carbon monoxide is toxic, invisible, and odourless.
It binds to haemoglobin in blood with an affinity 240 times greater than oxygen, preventing oxygen transport and causing hypoxia at the cellular level.
Even low concentrations can be fatal with prolonged exposure.

## Slide 13: Combustion reaction summary
Combustion type | Conditions | Chemical equation | By-products | Flame appearance | Hazard risk
Complete | Sufficient air supply, proper gas/air ratio, adequate ventilation | CH₄ + 2O₂ → CO₂ + 2H₂O + heat | CO₂, H₂O, heat | Blue with defined cones | Low
Incomplete | Poor ventilation, incorrect gas pressure, blocked flue, burner issues | CH₄ + O₂ → CO + H₂O + C + heat | CO, soot, unburned fuel, less heat | Yellow/Orange with unstable pattern | High

## Slide 14: Combustion reaction summary
Ventilation requirements
Connects to Unit K1.14 on Ventilation calculations and requirements. Proper air supply is critical for complete combustion.
Safety devices
Links to Unit K1.10 on Safety Devices including Flame Supervision Devices (FSD), CO alarms, and other protective measures.
Flue gas analysis
Connects to commissioning procedures where combustion analysis verifies safe operation within parameters.

## Slide 15: Why incomplete combustion is dangerous
Carbon monoxide (CO) poisoning
CO is a colourless, odourless gas produced during incomplete combustion.
It binds to haemoglobin in red blood cells, forming carboxyhaemoglobin (COHb), which prevents oxygen transport throughout the body.
This leads to cellular hypoxia and potential tissue damage.

## Slide 16: Why incomplete combustion is dangerous
Symptoms of CO poisoning
Headache and dizziness
Nausea and vomiting
Fatigue and confusion
Chest pain and rapid heartbeat
Seizures and loss of consciousness
Death at high concentrations

## Slide 17: Why incomplete combustion is dangerous
Risk factors that increase danger
Sleeping occupants may not notice symptoms
Confused with flu-like symptoms
Particularly dangerous for the elderly, children, and those with respiratory conditions

## Slide 18: Why incomplete combustion is dangerous
Technical hazards
Soot accumulation reduces heat transfer efficiency
Blocked heat exchangers lead to overheating
Potential for delayed ignition and flashback
Appliance breakdown and component failure
Failed safety checks during servicing
Appliance lockouts requiring an engineer to reset

## Slide 19: Why incomplete combustion is dangerous
Critical safety note
CO may be produced without any noticeable smell or flame change in some cases, particularly with high-efficiency condensing appliances.
This "silent killer" aspect makes regular CO detector installation and testing essential.

## Slide 20: Appliance design to prevent incomplete combustion
Design principles
Modern gas appliances incorporate numerous safety features and design elements specifically engineered to prevent incomplete combustion and protect users.
Burner technology
Precisely engineered burner ports and injectors ensure proper gas/air mixing. Pre-mix burners combine gas and air before combustion for optimal ratios. Venturi tubes create pressure differentials to draw in correct air volumes.

## Slide 21: Appliance design to prevent incomplete combustion
Monitoring systems
Flame rectification sensors verify proper combustion. Oxygen depletion sensors detect insufficient air. Temperature sensors monitor heat exchanger conditions. Pressure switches confirm proper air flow and flue operation.
Ventilation requirements
Room-sealed appliances separate combustion air from the living space. Powered flue systems ensure proper exhaust regardless of natural draft. Ventilation calculations determine the required free area for air supply. Specific installation clearances maintain airflow around appliances.

## Slide 22: Appliance design to prevent incomplete combustion
During installation
Verify correct gas type and pressure
Ensure appropriate ventilation
Install per manufacturer's instructions
Commission with combustion analysis
Test all safety devices

## Slide 23: Appliance design to prevent incomplete combustion
During servicing
Clean burners and injectors
Inspect heat exchangers for damage
Check flue integrity and termination
Verify safety device operation
Perform combustion analysis

## Slide 24: Knowledge check
Question 1
What is the chemical formula for carbon monoxide?
CO₂
C₂H₆
CH₄
CO

## Slide 25: Knowledge check
Question 2
What is a visual sign of incomplete combustion?
Blue flame
Soot around appliance
Cold flue pipe
Higher water pressure

## Slide 26: Knowledge check
Question 3
What gas is not produced during complete combustion?
Water vapour
Carbon dioxide
Carbon monoxide
Heat

## Slide 27: Knowledge check
Question 1
What is the chemical formula for carbon monoxide?
Explanation: Carbon monoxide (CO) consists of one carbon atom bonded to one oxygen atom. This partially oxidised form of carbon is the dangerous by-product of incomplete combustion.

## Slide 28: Knowledge check
Question 2
What is a visual sign of incomplete combustion?
Explanation: Soot (carbon particles) is produced during incomplete combustion when carbon isn't fully oxidized to CO₂. It appears as black deposits around the appliance, particularly on heat exchangers and flue ways.

## Slide 29: Knowledge check
Question 3
What gas is not produced during complete combustion?
Explanation: Complete combustion produces primarily CO₂ and H₂O. Carbon monoxide (CO) is specifically a product of incomplete combustion when there isn't enough oxygen for full oxidation of carbon atoms.

## Slide 30: Summary
You should now be able to:
Describe the process of complete and incomplete combustion.
Explain the chemical by-products of each reaction.
Identify visual and measurable signs of unsafe combustion.
Link combustion conditions to appliance performance and safety.

## Slide 31
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.