## Slide 1
Occupational Specialism: Gas Engineering
K1.14 Types of ventilation in relation to gas
PowerPoint 1.14a: Introduction to Ventilation in Gas Systems

## Slide 2: Starter
A customer installs a gas fire in their living room. A week later, they complain of headaches and find black marks on the wall near the appliance.
What might be wrong?
What might cause this?
What checks would you do first?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify different types of ventilation used in gas systems.
Describe the importance of adequate air supply in combustion.
Explain how poor ventilation can lead to unsafe situations.
Apply Building Regulations (Part J) to real-life scenarios.
You might also be able to:
Evaluate the adequacy of ventilation in a range of environments.

## Slide 4: Why ventilation matters in gas installations
Combustion requires oxygen; without it, incomplete combustion occurs.
Airflow is needed to dilute and remove combustion products.
Inadequate ventilation = risk of carbon monoxide (CO).
Room-sealed and open-flued appliances require different approaches.
Modern airtight homes need additional consideration (Part J update).

## Slide 5: Combustion requires oxygen
Complete combustion
Occurs when:
there is a sufficient supply of oxygen
the fuel burns efficiently.

## Slide 6: Combustion requires oxygen
Example (Methane): CH₄ + 2O₂ → CO₂ + 2H₂O
Products: Carbon dioxide (CO₂) and water (H₂O)
Clean blue flame
Maximum heat output
No harmful by-products.

## Slide 7: Combustion requires oxygen
Incomplete combustion
Occurs when:
There is an insufficient supply of oxygen
The fuel does not burn fully.

## Slide 8: Combustion requires oxygen
Products:
Carbon monoxide (CO)
Carbon (soot)
Less energy released
Yellow or orange flame
Risk of toxic emissions.

## Slide 9: Combustion requires oxygen
Why this matters in gas engineering
Adequate ventilation is critical to ensure enough air for combustion.
Incomplete combustion produces carbon monoxide, which is hazardous.
Appliance efficiency and safety depend on correct air-to-gas ratios.
Flue gas analysis is used during commissioning to verify combustion quality.

## Slide 10: Airflow is needed
Why airflow matters
Airflow has two critical functions in gas appliances and flue systems:
Oxygen supply – to support complete combustion.
Dilution and removal – to carry away combustion products safely.

## Slide 11: Airflow is needed
What happens without proper airflow?
Combustion gases (CO₂, CO, water vapour, unburned hydrocarbons) accumulate
Risk of flue gas spillage into occupied rooms
Condensation can damage the appliance and flue
Can lead to incomplete combustion or appliance lockout.

## Slide 12: Airflow is needed
Air movement affects:
Flue draught: natural or fan-assisted movement of gases through the flue.
Ventilation performance: air inlets and outlets must match appliance requirements.
Safety: inadequate removal of combustion products can result in CO poisoning.

## Slide 13: Airflow is needed
Design considerations
Flue systems must be sized and positioned correctly.
Openings must not be blocked or restricted.
Ventilation must suit the appliance type (e.g. open flued, room-sealed, flueless).
Mechanical ventilation (e.g. extract fans) must not cause negative pressure near appliances.

## Slide 14: Inadequate ventilation = risk of carbon monoxide
Understanding the link
Ventilation ensures that:
Combustion has a sufficient oxygen supply
Products of combustion are safely removed.
When ventilation is inadequate:
Oxygen levels drop
Incomplete combustion occurs
Carbon monoxide (CO) is produced.

## Slide 15: Inadequate ventilation = risk of carbon monoxide
Why CO is dangerous
CO is odourless, colourless, and tasteless
It binds with haemoglobin in the blood more readily than oxygen
Even low concentrations can cause illness or death.

## Slide 16: Inadequate ventilation = risk of carbon monoxide
Symptoms of CO exposure
Headaches, dizziness, nausea
Fatigue, confusion
Collapse, unconsciousness
Death with prolonged or high exposure

## Slide 17: Inadequate ventilation = risk of carbon monoxide
Engineering controls
Ensure ventilation meets the minimum requirements for appliance type.
Never block vents or flues.
Regularly inspect and maintain air pathways.
Fit carbon monoxide detectors in accordance with Building Regulations (e.g. Part J).
Follow manufacturer's instructions and IGEM/G/11 guidance for unsafe situations.

## Slide 18: Room-sealed and open-flued appliances
Open-flued appliances (Type B)
Draw combustion air from the room
Rely on natural draught to expel products of combustion
Sensitive to room ventilation and negative pressure

## Slide 19: Room-sealed and open-flued appliances
Design considerations
Adequate permanent ventilation into the room is essential.
Appliance location must avoid interference from extract fans or airtight construction.
Must comply with Part J of the Building Regulations and manufacturer’s air vent sizing.

## Slide 20: Room-sealed and open-flued appliances
Room-sealed appliances (Type C)
Completely sealed from the room
Air intake and flue outlet are ducted externally
Air is drawn directly from outside via a concentric or twin flue system.
Design considerations
No internal room air required for combustion
Ventilation may only be needed for cooling, compartment protection, or pipe ventilation
Safer for use in confined or airtight spaces.

## Slide 21: Room-sealed and open-flued appliances
Feature | Open-flued (Type B) | Room-sealed (Type C)
Air Source | Room | Outside via flue system
Ventilation Needed? | Yes – for combustion | Sometimes – for cooling only
Flue Type | Chimney or vertical flue | Balanced or concentric flue
Safety Sensitivity | High | Lower
Fan-Assistance Possible? | Optional | Often integrated

## Slide 22: Modern airtight homes need additional consideration
Why this matters
Newer homes are designed to be energy efficient and airtight, which reduces heat loss but also limits natural ventilation (also known as adventitious air). This directly impacts the safe operation of open-flued appliances.

## Slide 23: Modern airtight homes need additional consideration
Building regulations – Part J Update
Part J (Combustion Appliances and Fuel Storage Systems) includes specific guidance for:
Homes with a design air permeability of ≤ 5 m³/(h·m²)
These are classified as very airtight dwellings.
Key change: In such homes, the required size of permanent air vents for open-flued gas appliances must be increased to compensate for the lack of adventitious ventilation.

## Slide 24: Modern airtight homes need additional consideration
Ventilation design in airtight homes
Do not rely on natural leakage through walls, windows, or doors.
Calculate ventilation requirements precisely using manufacturer’s instructions or Approved Document J (Appendix C).
Ensure mechanical ventilation (such as MHVR or extract fans) does not cause negative pressure near appliances.

## Slide 25: Modern airtight homes need additional consideration
Risks of inadequate design in airtight homes
Incomplete combustion
Carbon monoxide build-up
Appliance malfunction or lockout
Violation of Building Regulations

## Slide 26: Combustion and Oxygen
Balanced combustion: CH₄ + 2O₂ → CO₂ + 2H₂O
Incomplete combustion: CH₄ + 1.5O₂ → CO + H₂O + soot
Signs of poor combustion:
Yellow flames, soot deposits, condensation on windows, headaches/drowsiness.

## Slide 27: Combustion and Oxygen
Role of oxygen in combustion
Oxygen is the reactant that enables the combustion process to begin.
The correct air-to-gas ratio is essential for efficient and safe operation.
Air contains ~21% oxygen; this is the primary source in most combustion systems.

## Slide 28: Combustion and Oxygen
Importance in gas systems
Correct oxygen levels ensure appliances operate safely and efficiently.
Oxygen deficiency can result in CO production, yellow sooty flames, and appliance failure.
Engineers must test flue gases and assess air supply during installation and commissioning.

## Slide 29: Types of air in combustion
Air type | Description
Primary air | Mixed with gas before ignition (e.g., at burner)
Secondary air | Mixed during combustion to ensure clean burn
Tertiary air | Excess air for complete combustion
Ventilation air | Fresh air supplied into room from outdoors
Dilution air | Drawn into flue to cool/dilute products of combustion
Adventitious ventilation | Unintended gaps/cracks — no longer relied on in modern homes

## Slide 30: Types of ventilation in gas systems
1. Permanent ventilation:
Fixed grilles or airbricks
Required for open flue appliances
Must not be blocked!

## Slide 31: Types of ventilation in gas systems
2. Mechanical ventilation:
Extractor fans, MVHR systems
Watch out for negative pressure zones.

## Slide 32: Types of ventilation in gas systems
3. Adventitious ventilation:
Occurs naturally (old homes)
No longer deemed sufficient by itself.
4. Appliance-specific (Room sealed):
Draws air directly from outside
Less dependent on room ventilation.

## Slide 33: Regulations and Standards
Building Regulations (Part J):
J1: Supply of air for combustion
J2: Discharge of products of combustion
Appendix C: Ventilation calculations for gas appliances.

## Slide 34: Regulations and Standards
IGEM/G/11 Guidance:
Unsafe classification for inadequate ventilation
Must act if combustion is compromised.
GS(I&U)R 1998:
Must ensure appliances are safe and adequately ventilated
Reg 26(9): Engineer’s duty to assess safety.
All must be considered when inspecting or commissioning systems.

## Slide 35: Real-world application
Scenario – Mark's loft boiler installation:
Mark installs a 24kW open-flued boiler in a converted loft space with no external ventilation.
Questions:
What concerns might this raise?
Would adventitious air be enough?
What calculation or guidance would you apply?

## Slide 36: Summary
You should now be able to:
Identify different types of ventilation used in gas systems.
Describe the importance of adequate air supply in combustion.
Explain how poor ventilation can lead to unsafe situations.
Apply Building Regulations (Part J) to real-life scenarios.
You might also be able to:
Evaluate the adequacy of ventilation in a range of environments.

## Slide 37
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.