## Slide 1
Occupational Specialism: Gas Engineering
K1.14 Types of ventilation in relation to gas
PowerPoint 1.14b: Ventilation Calculation Methods

## Slide 2: Starter
Tracy installs a 24kW open-flued boiler in a utility cupboard. There’s no visible ventilation. She says, ‘It should be fine – there’s a gap under the door!’
Discuss:
What’s the issue here?
How would you confirm whether ventilation is adequate?

## Slide 3: Objectives
By the end of this session, you should be able to:
Apply standard ventilation calculations to gas appliances.
Interpret appliance ratings and determine required vent areas.
Evaluate if existing ventilation meets current regulations.
Use IGEM/G/11, BS5440 Part 2 and Building Regulations Part J correctly.

## Slide 4: When is ventilation required?
Ventilation in gas systems
Ventilation ensures:
A sufficient supply of air for safe and complete combustion
The dilution and removal of combustion products
The cooling of appliances or components, where needed.

## Slide 5: When is ventilation required?
Ventilation is required when: 1. Combustion air is drawn from the room
Open-flued appliances (Type B) require permanent ventilation from outside to replace the air used in combustion.
2. An appliance is located in a confined or enclosed space
Appliances installed in cupboards, lofts, or compartments may need additional high and low-level ventilation to:
  supply combustion air
  prevent overheating.

## Slide 6: When is ventilation required?
3. Flueless appliances are used (Type A)
These appliances discharge combustion products directly into the room
Ventilation is mandatory to avoid CO and moisture build-up
Ventilation sizes are based on heat input (kW).
4. Modern airtight properties
New homes with high air tightness have reduced adventitious ventilation
Additional ventilation is needed even for open spaces (see Part J).

## Slide 7: When is ventilation required?
5. Mechanical extraction systems are present
Extract fans or mechanical ventilation can create negative pressure
Can lead to flue gas spillage in open-flued systems
A spillage or flue flow test must be carried out in these situations.
6. Manufacturer's instructions require it
Always follow the appliance-specific requirements. Ventilation must meet or exceed MI recommendations.

## Slide 8: When is ventilation required?
Not always required for:
Room-sealed (Type C) appliances in large, well-ventilated areas (Though cooling or compartment ventilation may still be needed).

## Slide 9: When is ventilation required?
Appliance type | Ventilation requirement
Room-sealed boilers | Minimal (draws air from outside)
Open-flue boilers | Requires permanent fixed ventilation
Flueless heaters | High air change rate required (usually not allowed)
Cookers in bedsits | Often restricted due to poor ventilation provision

## Slide 10: Gross and Net
When determining your ventilation needs, you can calculate based on either gross or net values.
Gross refers to the higher heating value, which includes the latent heat of water vaporisation during combustion, while net assumes that this latent heat from the water in the fuel is not recovered.
Therefore, for net calculations, allocate 5 cm² per kilowatt of input.
For gross calculations, allocate 4.5 cm² per kilowatt of input.
To convert gross to net, divide by 1.11.
To convert net to gross, multiply by 1.11.

## Slide 11: Gross and Net
A gas appliance like a BBU includes a data plate that provides technical information regarding the boiler's rating and performance.
​
For example, a data plate indicates that an appliance's maximum heat input is 21.8kW.
​​​

## Slide 12: Gross and Net
This appliance is an older model; the maximum input needs to be converted from gross to net.
21.8 ÷ 1.11 = 19.64 kW net.
Consequently, the required ventilation is 19.64 – 7 = 12.64.
Multiplying 12.64 by 5 gives 63.2 cm².

## Slide 13: Adventitious ventilation
Buildings allow drafts from outside, known as ‘adventitious ventilation’ (advent meaning air coming in from outside), which typically amounts to around 35cm² of free air.
When calculating air needed for combustion, the first 7kW of a gas appliance’s net input rating can be subtracted. For the remaining heat input, 5cm² of free air is required per kW, as shown below.
Example: A 16kW open flue boiler is installed in a room.
16kW – 7kW = 9kW.
Ventilation needed for 9kW = 9 x 5 = 45 cm².

## Slide 14: Adventitious ventilation
To guarantee sufficient combustion air, a vent with a free air area of 45cm² should be installed on an external wall.
Important: The vent must be clearly marked with its free air capacity.
When an open-flued appliance is fitted within a compartment, adventitious air is not subtracted from the calculation.​
This same guideline applies to:
flueless appliances like cookers
any appliance located in compartments
decorative fuel effect (DFE) gas fires.
​

## Slide 15: Decorative fuel effect
​DFE gas appliances are covered in BS 5871 Part 3 and it states that they require 100cm2 of ventilation unless manufacturers’ instructions (MI) differ.

## Slide 16: Calculation formula (open-flued appliances)
For open-flued gas appliances in rooms
This calculation ensures there is enough fresh air to support safe combustion when the appliance draws air from the room.
Standard formula (Natural Gas):
For an appliance installed in a room:
No vent required for the first 7 kW of rated input (this is assumed to come from adventitious air)
Then 5 cm² of free air is required per additional kW.

## Slide 17: Calculation formula (open-flued appliances)
Formula:
Minimum Ventilation Area (cm²) = 5 × (Appliance Input – 7 kW)
Worked example:
A 24 kW net open-flued boiler is installed in a room.
Step 1: Subtract 7 kW (adventitious air), 24 kW – 7 kW = 17 kW
Step 2: Multiply by 5 cm², 17 × 5 cm² = 85 cm² of free air required.
This vent must provide an unobstructed free area directly from the outside.

## Slide 18: Calculation formula (open-flued appliances)
Series configuration for open flue ventilation
When air is supplied from an external source, as illustrated in the example below, the dimensions of both the internal and external vents stay unchanged.

## Slide 19: Calculation formula (open-flued appliances)
Open flue ventilation in series
In the situation shown below, the external air vent 1 remains the same, but both internal vents 2 and 3 are 50% bigger than the external vent.

## Slide 20: Calculation formula (open-flued appliances)
Open flue ventilation in series
In the case of compartments, the vents in series rule does not apply.
Vents A and B are sized for the compartment as normal. However, both the internal vents 2 and 3 are still required to be 50% bigger than vent 1.

## Slide 21: Calculation formula (open-flued appliances)
Calculations for room-sealed appliances
No ventilation is needed when the appliance is installed within a room.
If the compartment has direct ventilation to the outside air, provide 5cm² of ventilation area per kW of rated heat input for both high and low settings.
When the compartment is ventilated through an internal space or room, ensure 10cm² of ventilation area per kW of rated heat input at both high and low levels.
Several manufacturers now indicate that ventilation is unnecessary for compartment installations due to the low surface temperatures of their room-sealed boilers.

## Slide 22: Compartment ventilation
A compartment is a space created to contain a gas appliance, such as a boiler room.
Typically, both high- and low-level ventilation are necessary unless the manufacturer’s guidelines specify differently.
The vents in an appliance compartment serve to supply air needed for complete combustion, ensure proper flue function, and help cool the appliance.
Compartments do not have an allowance for adventitious air.

## Slide 23: Compartment ventilation
Both air vents need to connect to the same room or area.
Both vents should be positioned on the same wall, facing outside.
When a compartment holds two or more appliances, their capacities must be combined to determine the required vent sizes.
If there is an open flue appliance in the compartment, additional combustion air will be necessary.
Range-rated appliances must be assessed based on their maximum input rating.

## Slide 24: Compartment ventilation
When determining the ventilation needed for an open-flued appliance with a 15kW input installed in a compartment with vents facing outside, the calculation involves multiplying the lower vent area by 10cm² per kilowatt of the appliance and the upper vent area by 5cm² per kilowatt. Thus:
10 × 15 equals 150cm² at the lower level and 5 × 15 equals 75cm² at the upper level.

## Slide 25: Compartment ventilation
For compartments with vents facing internally, the calculation changes to the appliance input rating multiplied by 20cm² for the lower vent and 10cm² for the higher vent. Hence:
20 × 15 equals 300cm² at the lower level and 10 × 15 equals 150cm² at the upper level.
Important note: No additional adventitious air allowance is permitted for compartments.

## Slide 26: Calculation formula (open-flued appliances)
Key notes:
For compartment installations, both high- and low-level vents are needed.
The vent must not be closeable or fitted with a flyscreen.
If a louvre grille is used, its free area must be confirmed (not just the physical size).

## Slide 27: Calculation formula (flueless appliances)
Ventilation should come directly from outside, and it must be possible to open a window or hinged panel in the same room, as required by Building Regulations.
Ventilation may only pass from one room to another if it is ducted.
Adequate room volume is necessary, and there are limits on the maximum input ratings for flueless appliances.
Smaller rooms require increased purpose-provided ventilation.
Manufacturer’s guidelines should always be followed.
Flueless space heaters are limited by the room volume in W/m³ and the rated input of the individual appliance.

## Slide 28: Calculation formula (flueless appliances)
Excerpt from table 4 of BS 5440 Part 2 showing the minimum permanent opening free area for flueless appliances.
Type of appliance | Maximum rated input limit (net) | Room volume (m3) | Permanent vent size (cm2) | Openable window or equivalent also required
Domestic oven, hotplate, grill or any combination thereof | None | < 5 | 100 | Yes
 |  | 5 to 10 | 50a | 
 |  | > 10 | Nil | 
Instantaneous hot water | 11kW | < 5 | Installation not permitted | Yes
 |  | 5 to 10 | 100 | 
 |  | > 10 to 20 | 50 | 
 |  | > 20 | Nil | 

## Slide 29: Calculation formula (flueless appliances)
For instance, a flueless water heater with a net output of 10kW placed in a room measuring 2m by 2m by 2.4m would result in a total room volume of 9.6m³.
Referring to the chart on the previous slide, it indicates that for a room size between 5m² and 10m², a ventilation area of 100 cm² is necessary, along with an openable window or a similar feature, such as a hinged panel.
If a domestic cooker is also installed in the same room, it would require a permanent vent providing 50 cm² in addition to an openable window or equivalent.
Further details, guidance, and ventilation requirements for other flueless appliances can be found in Table 4 of BS 5440 Part 2.

## Slide 30: LPG vs NG ventilation
Why the difference?
Ventilation requirements vary depending on the type of gas used due to differences in their physical and combustion properties.

## Slide 31: LPG vs NG ventilation
1. Natural Gas (NG)
Lighter than air (Relative Density ≈ 0.6)
Tends to rise and disperse
Commonly used in mains-supplied systems
Ventilation approach:
Standard sizing formulas apply (e.g. 5 cm² per kW above 7 kW for open-flued appliances), Vents are typically placed at high level, Combustion air supply must match appliance input and flue design.

## Slide 32: LPG vs NG ventilation
2. Liquefied Petroleum Gas (LPG)
Heavier than air (Relative Density ≈ 1.5 – 2)
Tends to sink and collect at low levels
Used where mains gas is unavailable (rural or off-grid locations)
Ventilation approach:
Same base sizing rules (5 cm²/kW above 7 kW)
Additional care is needed to prevent gas accumulation. Vents should be placed at a low level to allow heavier gas to escape. Basement installations are generally not permitted for LPG appliances.

## Slide 33: LPG vs NG ventilation
Feature | Natural Gas (NG) | Liquefied Petroleum Gas (LPG)
Relative Density | ~0.6 (lighter than air) | ~1.5–2.0 (heavier than air)
Gas behaviour | Rises and disperses | Sinks and collects
Ventilation Position | High-level vents preferred | Low-level vents essential
Storage | Mains supply | Cylinders or bulk tanks
Special Risks | Negative pressure rooms | Low-level accumulation
Basement use | Permitted | Not recommended

## Slide 34: LPG vs NG ventilation
Design and safety notes
Always follow the manufacturer’s instructions.
Ventilation must comply with Part J, BS5440 Pt2 and IGEM/UP/10.
LPG appliances must have appropriate leak detection, shut-off controls, and be in well-ventilated locations.

## Slide 35: Appliance location factors
Factor | Ventilation effect
Small rooms | Less air available, may need venting to outside
Cupboards / boxed-in areas | Need high/low vents or louvre doors
Lofts / basements | May require mechanical ventilation
MVHR systems installed | Can create negative pressure – must be assessed

## Slide 36: Grille sizing and selection
Purpose of ventilation grilles
Ventilation grilles are used to allow a controlled flow of air into or out of a space for:
Combustion air supply
Dilution and cooling
Safe removal of combustion products.
Correct sizing and selection are essential to ensure the required free air area (cm²) is achieved without restriction.
.

## Slide 37: Grille sizing and selection
1. Free area vs physical size
Free area is the actual open space that allows air to pass through.
The grille’s physical size (e.g. 225 mm × 225 mm) is not the same as its free area.
Grille apertures must admit a 5mm ball bearing but not a 10mm ball bearing.
Manufacturers must provide a free area rating for each grille. Example: A 225 × 225 mm louvre grille may only offer 60% free area → Physical size = ~50,000 mm² → Free area = 30,000 mm² = 300 cm²
.

## Slide 38: Grille sizing and selection
2. Sizing based on appliance heat input
Follow these basic rules (for open-flued appliances):
No vent needed for first 7 kW
5 cm²/kW required above 7 kW (natural gas)
LPG appliances may require low-level grille positioning
Compartment installations may need high and low-level vents.

## Slide 39: Grille sizing and selection
3. Selecting the right grille type
Grille Type | Characteristics | Suitability
Louvre Grille | Slatted design, low visibility, reduced airflow | Common but must check free area
Hit & Miss Vent | Manually openable – not allowed for combustion | Not suitable for gas appliances
Flyscreen Vent | Has mesh screen – not allowed for combustion | Risk of blockage and restriction
Terracotta Grille | Clay material, often used in older builds | Poor accuracy of free area
Unsleeved Opening | A hole without a grille – not compliant | Fails Building Regs / Gas Safety
Fixed Open Grille | Compliant permanent solution | Best practice for safety

## Slide 40: Grille sizing and selection
4. Positioning
Low level: For LPG and some cooling air requirements
High level: For heat and natural gas combustion air
Grilles should be:
  Unobstructed by insulation, furniture, or finishes
  Located in accordance with MI, Part J, and IGEM/UP/10.

## Slide 41: Grille sizing and selection
5. Installer responsibilities
Confirm required free area (cm²) from ventilation calculation.
Select appropriate grille with certified free area.
Avoid DIY, non-compliant, or decorative-only grilles.

## Slide 42: Ventilation general requirements
Ventilation must be permanent: Grilles or vents must be non-adjustable and always open.
Any duct or pipe passing through a cavity wall must be sleeved to maintain structural integrity and airflow.
Ventilation must be to outside air: Internal air transfer is not acceptable for combustion air.
Grilles must be correctly sized: Based on appliance type, flue type, and heat input (net or gross).
Positioning: Vents should be placed to avoid draughts, noise, or obstruction.

## Slide 43: Inspection of existing installations
Inspection of existing installations – ventilation checklist
When inspecting existing installations, ventilation must be checked thoroughly to ensure compliance and safety. Use the following inspection criteria:
1. Ventilation path is unobstructed
Check that grilles, ducts, and air inlets/outlets are free from blockage, insulation, or covering.
Ensure airflow is continuous and not impeded by debris, furniture, or structural modifications.

## Slide 44: Inspection of existing installations
2. Vent size matches appliance heat input
Confirm that the permanent ventilation size (in cm²) meets or exceeds the calculated requirement.
Use the correct sizing rule: e.g. 5 cm² per kW above 7 kW (for open-flued NG appliances).

## Slide 45: Inspection of existing installations
3. Labelling is present and visible
Grilles, duct covers, or ventilated compartments should be clearly marked as permanent ventilation.
Any compartmented appliance must have appropriate warning labels (e.g. 'Do Not Block Vent').

## Slide 46: Inspection of existing installations
4. No evidence of tampering or sealing
Check for signs that vents have been covered, closed, or restricted (e.g. taped over, furniture pushed against them).
Hit-and-miss vents or closable grilles are not permitted for combustion ventilation.

## Slide 47: Inspection of existing installations
5. Confirm against manufacturer’s instructions and IGEM/G/11
Review the appliance MI for any specific ventilation requirements.
Check compliance with IGEM/G/11, which governs unsafe situations. Improper ventilation may warrant AR or ID classification.

## Slide 48: Inspection of existing installations
Inspection outcome
If ventilation is found to be non-compliant, the engineer must:
classify the installation (AR or ID)
isolate if necessary
complete warning notices and notify the responsible person.

## Slide 49: Inspection of existing installations
Georgia is replacing a 28kW open-flued fire. The room has a 100 cm² wall grille.
Questions:
Is the ventilation sufficient?
What else should be inspected?
Would you class the system as, At Risk or ID?

## Slide 50: Summary
You should now be able to:
Apply standard ventilation calculations to gas appliances.
Interpret appliance ratings and determine required vent areas.
Evaluate if existing ventilation meets current regulations.
Use IGEM/G/11 and Building Regulations Part J correctly.

## Slide 51
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.