## Slide 1
Occupational Specialism: Gas Engineering
K1.26 Safe storage and supply of fuel source
PowerPoint 1.26b: LPG – Liquefied Petroleum Gas

## Slide 2: Starter
Georgia is fitting a new LPG boiler in a static caravan. She places two cylinders inside a rear cupboard under the sink, with a regulator fitted to the first cylinder.
What safety regulations are being breached?
Where should cylinders be stored?
What risks are introduced by incorrect storage?

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe the safe storage and handling requirements for LPG cylinders and tanks.
Explain the positioning, ventilation and signage regulations for LPG installations.
Identify the correct equipment used for LPG supply (regulators, pigtails, changeover valves).
Evaluate storage scenarios for compliance with standards and safety best practices.

## Slide 4: What are the advantages of selecting LPG instead of natural gas?
In certain rural parts of the UK, access to the natural gas network may be limited. As a result, alternative fuel supply options should be explored, including:
​Biomass
Solid fuels
Fully renewable technologies
LPG

## Slide 5: What is LPG?
Liquefied Petroleum Gas = stored under pressure as a liquid, used where NG is unavailable.
Types: Propane (C₃H₈) and Butane (C₄H₁₀).
Delivered via:
  Cylinders (single or twin).
  Bulk tanks (above ground or underground).

## Slide 6: Factors to consider regarding LPG
The primary factors to consider include:
LPG storage tanks function within a pressure range of 2 to 9 bar.
LPG appliances are engineered to operate at pressures of 37 mbar (± 5 mbar) for propane and 28 mbar (± 5 mbar) for butane.
Since LPG contains more energy per volume than natural gas (NG), smaller amounts are needed to produce an equivalent amount of heat.
The relative density of LPG (Liquefied Petroleum Gas) is typically around 1.5 to 2.0 compared to air, depending on the propane–butane mix.

## Slide 7: Placement of bulk storage tanks
LPG bulk storage tanks must be positioned at a distance from the property as well as from any drains and gullies.
Additionally, it is important to ensure that access for refilling the tank is maintained, with a minimum width of 2.75 metres to accommodate delivery vehicles.

## Slide 8: Placement of bulk storage tanks
Above-ground or underground.
Must be positioned with clearances (as per UKLPG code of practice):
  3 m from buildings or boundaries.
  1.5 m clearance for cylinder supply pipe.
Protected from impact or tampering (e.g. barriers, bollards).
No ignition sources or flues nearby.
Fill point and pressure relief vent must face away from the building.

## Slide 9: Placement of bulk storage tanks
Hazards and Safety Risks
Accumulation in low areas → explosion risk.
Over-pressure if regulators fail.
Fire hazard from poor storage.
Incorrect pipe materials or fittings.
Vandalism or theft of outdoor cylinders.

## Slide 10: Pressure reduction
LPG is typically delivered at pressures up to 9 bar, so its pressure must be lowered before entering the premises.
This pressure reduction is managed by a pressure regulator to ensure a steady pressure. In bulk storage setups, a two-stage system is employed:
The first stage regulator, attached to the storage vessel, reduces the vessel pressure to a medium level below 2 bar.
The second stage regulator further lowers this medium or intermediate pressure to the operating pressure of 37 mbar. These regulators also incorporate UPSO and OPSO safety features.

## Slide 11: Installations with multiple cylinders
Multi-cylinder setups must be mounted on walls that provide adequate fire resistance, typically 30 minutes.
It is also important to place them away from drains and gullies.
Cylinders ought to be installed as near as possible to the point where the pipework enters the building.

## Slide 12: Installations with multiple cylinders
Installations with multi-cylinders should be connected in service and reserve arrangements. This allows cylinders to be changed over without disrupting the whole system.
BS5482 offers a code of practice to the installation of LPG systems and pipework up to 25mm diameter.

## Slide 13: Cylinder storage requirements
Location:
  External to building
  Well-ventilated
  Upright, stable, and secure.
Distance from:
  Openings, airbricks, or ignition sources
  Drains or basement-level voids.
Ventilation: Must allow LPG to disperse safely (LPG is heavier than air).
Storage cage: Lockable and weather-protected with signage.

## Slide 14: Components for cylinder supply
Component | Purpose
Regulator | Reduces pressure from 37–75 mbar to 30/50 mbar.
Pigtails | Flexible copper hoses connecting cylinder to valve.
Changeover Valve | Automatically switches to reserve cylinder.
Excess Flow Valve | Shuts off gas if pigtail ruptures or leaks.
Labels & Signage | Alert users to hazards and cylinder contents.

## Slide 15: Key regulations and standards
UKLPG Code of Practice 1 & 24
Part J – Combustion Appliances and Fuel Storage.
GSIUR 1998 – Installation and Use.
BS 6891 – Pipework and safety requirements.
Manufacturer's installation instructions (MI).

## Slide 16: Summary
You should now be able to:
Describe the safe storage and handling requirements for LPG cylinders and tanks.
Explain the positioning, ventilation and signage regulations for LPG installations.
Identify the correct equipment used for LPG supply (regulators, pigtails, changeover valves).
Evaluate storage scenarios for compliance with standards and safety best practices.

## Slide 17
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.