## Slide 1
Occupational Specialism: Gas Engineering
K1.28 Fault-finding techniques, their suitability for different situations and how they are applied in practice
PowerPoint 1.28d: Practical diagnosis, planned maintenance and real-world faults

## Slide 2: Starter
Scenario
Ash attends a call-out for no heating. He resets the boiler and it works. Two days later, the fault returns.
Consider:
Was this issue fixed or merely reset?
What else should Ash have investigated?
What could he do differently to prevent a repeat call-out?

## Slide 3: Objective
By the end of this session, you will be able to:
Apply fault-finding knowledge to real case scenarios.
Explain how planned maintenance reduces system faults.
Use manufacturer resources and digital tools to inform diagnosis.
Evaluate the effectiveness of their diagnostic process.

## Slide 4: The practical diagnostic sequence
Initial assessment
User questioning – understand fault history
Safety checks (gas/electric isolation, tightness)
Visual inspection of components and connections
Information gathering
Review manufacturer instructions
Check service history and previous faults
Electrical and pressure tests

## Slide 5: The practical diagnostic sequence
Detailed analysis
Component testing (sensor, fan, valve, PCB)
Action – clean, adjust or replace components
Retest system and record outcomes

## Slide 6: Component analysis
Critical components to test
PCB: Voltage outputs, error code history
Fan: Rotation, electrical resistance, obstruction
Gas Valve: Operation, solenoid functionality
NTC Sensors: Resistance values, connections
Pressure Switch: Continuity testing
Electrodes: Gap measurement, condition
Condensate Trap: Blockages, proper drainage

## Slide 7: Planned maintenance strategies
Annual servicing
Conduct thorough inspections in line with manufacturer instructions (MI). Document baseline readings for future reference.
Component cleaning
Systematically clean the burner, condensate trap, heat exchanger, and electrode. Inspect for damage or deterioration.

## Slide 8: Planned maintenance strategies
Filtration checks
Inspect and clean magnetic filters, system strainers, and condensate paths. Replace as needed to prevent blockages.
Data logging
Record pressure readings, flue gas analysis ratios, error codes, and customer reports for trend analysis.
Well-executed planned maintenance significantly reduces emergency call-outs and provides valuable diagnostic history.

## Slide 9: The benefits of proactive maintenance
Regular planned maintenance delivers multiple benefits beyond fault prevention, with significant impact on system reliability and efficiency.
Engineers should communicate these advantages to customers to justify the importance of annual servicing.

## Slide 10: Using manufacturer and online resources
Resource | Purpose | Best Practice
Manufacturer Flow Charts | Fault code sequences and diagnostic pathways | Follow systematically; don't skip steps
Technical Apps & Portals | Wiring diagrams, training modules, specifications | Download for offline access before site visits
YouTube (verified content) | Visual how-to guides from manufacturers | Verify source is official (e.g. Ideal, Vaillant)
Professional Forums | Peer feedback on common appliance faults | Cross-reference advice with manufacturer guidance
Installer Helplines | Product-specific advice from engineers | Record case numbers and recommendations
⚠️ Always use official sources only — avoid unsafe advice ⚠️

## Slide 11: Digital tools in diagnostics
Essential digital diagnostic tools
Digital manometers: Precision pressure measurement with data recording capability
Multifunction testers: Combined electrical testing for multiple parameters
Thermal cameras: Identify heat distribution issues and blockages
Combustion analysers: Digital FGA with Bluetooth connectivity
Manufacturer apps: Direct access to technical libraries and diagnostics

## Slide 12: Case study 1: No ignition after service
Symptoms
Boiler attempts ignition but fails to light
Error code indicates ignition failure
Problem began immediately after annual service
Intermittent successful ignition followed by failure

## Slide 13: Case study 1: No ignition after service
Diagnostic process
Visual inspection of gas supply and connections
Multimeter test of ignition electrode circuit
Measured electrode gap with feeler gauge
Inspection revealed electrode disturbed during cleaning

## Slide 14: Case study 1: No ignition after service
Resolution
Re-positioned electrode to correct specification (3-4mm)
Cleaned electrode tip to remove carbon deposits
Tested ignition sequence through multiple cycles
Documented in service record with before/after measurements
This case demonstrates how even minor disturbances during routine maintenance can create new faults if not properly verified.

## Slide 15: Case study 2: Intermittent hot water
Symptoms
Customer reports inconsistent hot water temperature. Initially hot, then rapidly cooling. System pressure is normal. No error codes displayed.
Diagnostic process
Tested DHW NTC sensor resistance – within range
Checked diverter valve operation – functioning correctly
Measured flow rate at outlets – significantly reduced
Inspected DHW flow sensor – limescale build-up discovered

## Slide 16: Case study 2: Intermittent hot water
Resolution
Removed and descaled DHW flow sensor
Cleaned filter mesh at cold water inlet
Fitted inline scale inhibitor to prevent recurrence
Flow rate returned to manufacturer specification
Advised customer on water hardness management

## Slide 17: Case study 3: Yellow flame and lockout
Initial symptoms
Boiler displaying lockout code. Customer reports unusual smell. Last service over 18 months ago. System in hard water area with poor ventilation.
Visual inspection
Yellow flame visible through inspection window. Cabinet shows signs of soot. Condensate pipe partially blocked. Flue terminal partially obstructed by vegetation.

## Slide 18: Case study 3: Yellow flame and lockout
Testing process
Flue gas analysis shows high CO readings. Combustion ratio outside parameters. Gas pressure test is normal. Air intake partially restricted.
Root cause
Burner ports are blocked with debris and carbon buildup. Primary heat exchanger fins restricted. Insufficient air for complete combustion, resulting in partial burning.

## Slide 19: Case study 3: Yellow flame and lockout
Resolution
Cleaned burner ports thoroughly. Cleared heat exchanger passages. Cleaned condensate trap. Cleared flue terminal. Retested combustion – now within parameters.

## Slide 20: Common fault patterns by manufacturer
Manufacturer | Common Fault | Typical Cause | Diagnostic Approach
Worcester Bosch | EA/EC Fault Codes | Electrode issues | Check gap, clean, test resistance
Vaillant | F.75 Error | Pump or pressure sensor | Check wiring, test sensor resistance
Ideal | L2 Lockout | Ignition failure | Gas pressure, electrode, flame sensing
Baxi | E133 Code | Gas supply issues | Check inlet pressure, valve operation
Glow-worm | F.28 Error | No gas ignition | Electrode check, gas valve testing
Understanding manufacturer-specific fault patterns can significantly accelerate diagnosis. Always cross-reference with current technical bulletins as common faults may change with product revisions.

## Slide 21: Diagnostic decision trees
Decision trees provide a systematic approach to complex diagnostics.
Follow each branch methodically, conducting all specified tests before proceeding.
Never skip steps based on assumptions. Document your path through the decision tree for future reference.

## Slide 22: Practical workshop: Systematic diagnosis
Initial consultation
Conduct a thorough interview with the "customer" (peer). Ask specific questions about fault symptoms, timing, any pattern to occurrences, and recent system changes.
Safety assessment
Perform proper isolation procedures. Conduct gas tightness testing. Ensure electrical safety before proceeding with diagnostics.

## Slide 23: Practical workshop: Systematic diagnosis
Systematic testing
Follow manufacturer diagnostic sequence. Document all test readings and observations. Use proper test equipment and record all values.
Solution implementation
Select appropriate repair method. Document all components replaced or adjusted. Test thoroughly after repair completion.
Workshop exercise: In pairs, one trainee describes a fault scenario while the other follows the diagnostic sequence to troubleshoot. Switch roles and repeat with a different fault.

## Slide 24: Practical reflection task
Recall a real fault experience
Think of a fault you've encountered in workshop or work placement. This could be a successful diagnosis or one that proved challenging.
Apply the 8-Stage model

## Slide 25: Practical reflection task
Apply the 8-Stage model
What questions did you ask the user?
What safety checks did you perform?
What did your visual inspection reveal?
What documentation did you consult?
What tests did you conduct?
Which components did you analyse?
What action did you take?
How did you verify the fix?

## Slide 26: Preventative vs. Reactive maintenance
Scheduled
Annual servicing based on manufacturer guidelines. Documented history of system performance.
Proactive
Identifying potential issues before they cause failure. Monitoring of performance trends.
Predictive
Using data to forecast when components are likely to fail. Scheduling replacement before breakdown.

## Slide 27: Preventative vs. Reactive maintenance
Reactive
Emergency response to unexpected failures. Higher cost and customer dissatisfaction.
Well-documented maintenance helps establish baseline performance and identify subtle changes that may indicate developing faults. Each preventative approach reduces the likelihood of reactive call-outs.

## Slide 28: Comprehensive system health check
Mechanical components
Heat exchanger: Check for corrosion, blockages
Pump: Assess for noise, proper rotation
Gas valve: Verify operation, test modulation
Expansion vessel: Check pressure, membrane condition
Fan: Test for noise, vibration, free movement

## Slide 29: Comprehensive system health check
Hydraulic system
System pressure: Verify operating range
Flow rates: Measure at key test points
Water quality: Check for discoloration, debris
Inhibitor levels: Test and top up as needed

## Slide 30: Comprehensive system health check
Electrical system
PCB: Inspect for damage, burning, loose connections
Sensors: Test resistance values against specification
Wiring: Check for fraying, damage, loose connections
Controls: Verify operation of thermostats, timers

## Slide 31: Comprehensive system health check
Combustion assessment
Flue gas analysis: CO, CO₂, ratio measurements
Gas pressure: Standing and working pressures
Burner condition: Inspect flame pattern, colour
Ventilation: Verify adequate air supply

## Slide 32: Summary: The complete diagnostic approach
Mastery
Confidently resolve complex faults through critical thinking
Diagnostic process
Follow complete diagnostic sequences with thorough testing
Technical resources
Effectively use manufacturer instructions, tools, and diagnostic logic

## Slide 33: Summary: The complete diagnostic approach
Preventative maintenance
Implement comprehensive servicing to prevent common faults and system failures.
Reflective practice
Continuously evaluate what went well and identify areas for improvement in the diagnostic approach.
A professional gas engineer combines technical knowledge with systematic methodology, supported by proper documentation and ongoing professional development.

## Slide 34: Summary
You should now be able to:
Follow a complete diagnostic process.
Use MI, tools, and technician logic to solve faults.
Carry out preventative servicing.
Reflect on what went well and what could be improved.

## Slide 35
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.