T Level Technical Qualification in Building Services Engineering for Construction (Level 3)

Skills Practice Workbook for Learners

Gas Engineering

Practical Training

Learner name:

Centre name:

Contents

Task 1 - Health & Safety	6

Task 2 - Access Equipment	7

Task 3 - Risk Assessment	8

Task 4 - Method Statement	10

Task 5 - Personal Protective Equipment	11

Task 6 - Identification of Tools	13

Task 7 – Access Equipment Ladders	16

Task 8 - Liquified Petroleum Gas (L.P.G.) equipment	17

Task 9 – Fire Extinguishers	21

Task 10 – Mobile scaffold	22

Task 11 - Safe Isolation Procedure	25

Task 12 - Measuring and Cutting	26

Task 13 - Fittings	27

Task 14 - X Dimensions and Z Dimensions	31

Task 15 – Fixings	32

Task 16 - Decommissioning	34

Task 17 - Copper Compression	36

Task 18 - Copper Soldering	38

Task 19 - Copper Bending	40

Task 20 - Copper Frame	42

Task 21 - Plastic Push Fit	44

Task 22 - Steel bending	46

Task 23 - Steel jointing	48

Task 24 – Combined Frame	50

Task 25 - Electrical tools	53

Task 26 - Fittings And Jointing Materials Identification	54

Task 27 - Termination of BS1363 plug top	55

Task 28 - Operating a U gauge and digital manometer	57

Task 29 - Gas meters and enclosures	59

Task 30 - Let-by testing and tightness testing – low pressure	60

Task 31 - Let-by testing and tightness testing – medium pressure	61

Task 32 - Purging	62

Task 33 - The installation pipework	65

Task 34 - Installing a boiler	74

Task 35 - Gas Rating	80

Task 36 - Gas Flow and Pressure Loss	84

Task 37 - Pressure Regulators	86

Task 38 - Servicing a boiler	89

Task 39 - Flues and chimneys	94

Task 40 - Flues and chimneys part 2	95

Task 41 - Ventilation	101

Task 42 - Installing a gas multipoint water heater	105

Task 43 - Servicing a gas multipoint water heater	109

Task 44 - Electrical safe isolation procedure and Electrical Testing	112

Task 45 - Recognition of controls	116

Task 46 - IGEM G/13 Procedures	121

Task 47 - Gas Safety (Installation and Use) Regulations	123

Task 48 - Written report of maintenance activity	131

# Task summary and progress tracker

|  | Task | Page number | Date complete |
| --- | --- | --- | --- |
| 1 | Workshop health and safety procedures |  |  |
| 2 | Access equipment |  |  |
| 3 | Risk assessment |  |  |
| 4 | Method statement |  |  |
| 5 | Personal protective equipment |  |  |
| 6 | Identification of Tools |  |  |
| 7 | Access equipment ladders |  |  |
| 8 | L.P.G equipment |  |  |
| 9 | Fire extinguishers |  |  |
| 10 | Mobile scaffold |  |  |
| 11 | Safe isolation procedure |  |  |
| 12 | Measuring and cutting |  |  |
| 13 | Fittings |  |  |
| 14 | X dimensions & Z dimensions |  |  |
| 15 | Fixings |  |  |
| 16 | Decommissioning |  |  |
| 17 | Copper compression |  |  |
| 18 | Copper soldering |  |  |
| 19 | Copper bending |  |  |
| 20 | Copper frame |  |  |
| 21 | Plastic push fit |  |  |
| 22 | Steel bending |  |  |
| 23 | Steel jointing |  |  |
| 24 | Combined frame |  |  |
| 25 | Electrical tools |  |  |
| 26 | Fitting and Jointing Materials Identification |  |  |
| 27 | Termination of Plug Top |  |  |
| 28 | Operating a U Gauge and Digital Manometer |  |  |
| 29 | Gas meters and enclosures |  |  |
| 30 | Let-by testing and tightness testing – low pressure |  |  |
| 31 | Let-by testing and tightness testing – medium pressure |  |  |
| 32 | Purging |  |  |
| 33 | The installation pipework |  |  |
| 34 | Installing a boiler |  |  |
| 35 | Gas rating |  |  |
| 36 | Gas flow and pressure loss |  |  |
| 37 | Pressure regulators |  |  |
| 38 | Servicing a boiler |  |  |
| 39 | Flues and Chimneys Part 1 |  |  |
| 40 | Flues and Chimneys Part 2 |  |  |
| 41 | Ventilation |  |  |
| 42 | Installing a gas multi point water heater |  |  |
| 43 | Servicing a gas multi point water heater |  |  |
| 44 | Electrical safe isolation procedure and electrical testing |  |  |
| 45 | Recognition of controls |  |  |
| 46 | IGEM G/13 procedures |  |  |
| 47 | Gas Safety (Installation and Use) Regulations |  |  |
| 48 | Written report of maintenance activity |  |  |

# Task 1: Workshop induction: health and safety procedures

Health and safety are very important in any workshop or workplace. All rules must be followed to ensure everyone's safety.

The primary legislation that covers health and safety in such surroundings is the Health and Safety at Work Act (1974).

To establish a safe working environment, familiarise yourself with the workshop and complete the following tasks:

1.	Record the position of any emergency stop buttons in the workshop.

2.	List the types of fire extinguishers and the colour codes that identify them.

3.	Find where the first aid box is kept and suggest what should be kept in it.

4.	List the main items of protective clothing you are expected to wear.

5.	Write out the emergency evacuation procedure for the workshop and where the assembly point is.

6.	Identify who to immediately inform in the event of an accident.

7.	Find out where we record any accidents that may occur in the workshop.

8.	Determine the first action to take if someone receives an electric shock.

9.	Familiarise yourself with the emergency procedure to summon help in your place of learning.

10.	Draw two safety signs in the workshop and explain their meaning.

| Answers: |  |  |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |
| 8 |  |  |
| 9 |  |  |
| 10 | 1. | 2. |

As an employee (learner) you have legal duties too. They include: - Taking reasonable care for your own health and safety and that of others who may be affected by what you do or do not do; - Co-operating with your employer on health and safety; - Correctly using work items provided by your employer, including personal protective equipment, in accordance with training or instructions; and - not interfering with or misusing anything provided for your health, safety or welfare.

Who is responsible for health and safety on site?

Which types of accident need to be recorded and where do we record the information?

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 2: Access equipment

Below are two types of ladders. What are they called, and what checks would you carry out before you use them?

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 3: Risk assessment

Risk assessments are something you are required to carry out by law; however, if you employ fewer than five people, you don't have to write anything down. To carry out a risk assessment you need to think about the things that might cause harm to people and decide if you are taking reasonable steps to prevent the harm.  For certain risks, specific regulations require particular control measures to be put in place for example, working in a confined space.

Hazard - anything that may cause harm.

Risk - the chance, high or low, that somebody could be harmed.

Complete the following risk assessment template for the workshop you are working in.

| What are the hazards? | Who might be harmed and how? | What are you already doing? | Do you need to do anything else to control this risk? | Action by who? | Action by when? | Done |
| --- | --- | --- | --- | --- | --- | --- |
| Slips and trips | Staff and visitors may be injured if they trip over objects or slip on spillages. | General good housekeeping is carried out. All areas well lit. No trailing leads or cables. Staff keep work areas clear, e.g. no boxes left in walkways. Deliveries are stored immediately. Safety signs displayed throughout. | Arrange for the loose carpet tile on the second floor to be repaired or replaced. | All staff and supervisors are to monitor. Manager. |  |  |

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 4: Method statement

A method statement, also known as a “safe system of work," is a document that details how to carry out a task safely. It outlines all the hazards involved and includes a step-by-step guide on how to carry out the task safely. The method statement ensures that the risks and precautions required of all those involved in the task are effectively communicated.

Method statements also detail the control measures introduced to ensure the safety of anyone who is affected by the task.

A method statement includes the following information:

- Description/overview of works

- Location

- Start and finish time

- Supervisor name and contact details

- Resources required

- Referenced to the risk assessment conducted for the task

- Control measures

- PPE

- Emergency actions

- Welfare and first aid measures

Task: Use of a power drill:

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 5: Personal Protective Equipment (PPE)

Identify the PPE and describe its use.

| PPE Item | Name/Use |
| --- | --- |

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 6: Identification of tools

Identify the tools and describe their use.

| Tools/Equipment | Name/Use |
| --- | --- |

What would you do if you discovered a tool that you did not know what it is used for or how to use?

……………………………………………………………………………………..

Why is it important to check tools are safe and in good working order after using them?

……………………………………………………………………………………..

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 7: Access equipment ladders

Label numbers 1 to 4 correctly.

1.

2.

3.

4.

List four safety checks required prior to using stand steps:

| Safety Check |  |
| --- | --- |
| 1 |  |
| 2 |  |
| 3 |  |
| 4 |  |

# Task 8: Liquified Petroleum Gas (L.P.G.) equipment

You will be required to use this equipment when soldering, however there is a safe method of use that you must demonstrate before you will be able to solder.

What checks must be made prior to using this equipment?

Describe the commissioning and decommissioning procedures.

Commissioning

Commissioning

Decommissioning

Decommissioning

What can be used to protect the fabric of the building?

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

Gas Cylinder Safety Report

The following information should be provided:

- Assess Situations & Equipment for Safety

| Identify whether the following situation is safe or unsafe |  |
| --- | --- |
| Situation | Safe or Unsafe? |
| Full & empty gas cylinders are stored in an outside cage with a roof that is locked and far away from combustible materials overnight. |  |
| Cylinders are being transported around a building site on three wheeled trolleys. |  |
| A lot of oxygen cylinders are stored in a basement with one small door and no windows. The gas bottles are fully strapped up horizontally and cannot roll. |  |
| A gas cylinder is often subjected to shocks and falls on site. |  |
| A tradesman is carrying an oxyacetylene bottle by its control valve. |  |
| Cylinders are stored in a cage on a building site. A strong wall shields the cylinders from direct sunlight. |  |
| Gas cylinders are stored close to a welding area that is used regularly. |  |
| Oxygen, acetylene & LPG cylinders are all stored together in a well-ventilated area. |  |
| Gas cylinders are stored outside in a cage. The cage is designed so that the gas bottles are stacked horizontally four cylinders high. They are secured to prevent falling onto the soft ground below. |  |
| Trolleys used for transporting cylinders should be manufactured to: | BS |

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 9: Fire extinguishers

The following information should be provided:

Classification of fires and fire extinguisher procedures

| Identify the following information |  |  |  |
| --- | --- | --- | --- |
| Class Of Fire | Source Of Fuel | Colour of Fire Extinguisher Necessary | Contents of Fire Extinguisher |
| Class A |  |  |  |
| Class B |  |  |  |
| Class C |  |  |  |
| Class D |  |  |  |
| Class E |  |  |  |
| Class F |  |  |  |

Explain the correct procedure for using a fire extinguisher to tackle a small solid fuel fire:

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 10: Mobile scaffold

WAH Regulations 12(7)

These regulations requires that a Mobile Access Tower be inspected and approved by a competent person and within 24 hours a report thereof be provided to the person on whose behalf the inspection was carried out.

It is also required that a tag system be attached to the tower recording that an inspection has taken place and that there is an inspection checklist in existence.

| The timing of inspections |  |
| --- | --- |
| This checklist refers to one off the following timings (please tick as appropriate): |  |
| When the tower has been built and taken into us e for the first time | ☐ |
| After any substantial addition, dismantling or other alteration | ☐ |
| After any event likely to have affected it strength or stability | ☐ |
| At regular intervals NOT exceeding 7 days | ☐ |

| Details of the competent person making this inspection |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Name |  |  | PASMA No. |  |  |
| Date of inspection |  |  | Time |  |  |
| Person to whom this inspection was carried out |  |  |  |  |  |
| Name |  |  | Organisation |  |  |
| Description of the tower |  |  |  |  |  |
| Double/single width |  | Height |  | Mobile | ☐ |
|  |  |  |  | Static | ☐ |
| Tower Manufacturer |  |  | Type | Aluminium | ☐ |
|  |  |  |  | GRP | ☐ |
| Location of tower at time of inspection |  |  |  |  |  |

| The following items to be checked | Yes | No |
| --- | --- | --- |
| - Do you have a copy of the manufacturers instruction manual (MIM) to enable you check the tower? | ☐ | ☐ |
| - Does a risk assessment for the tower exist? | ☐ | ☐ |
| - Check that the environment has no detrimental effect on the safe use of the tower. | ☐ | ☐ |
| - Are the castors or base plates fully in contact with the ground and bearing their share of the weight of the tower and that all 4 brakes are applied? | ☐ | ☐ |
| - Are the adjustable legs only being used to level the tower and not for gaining height? | ☐ | ☐ |
| - Is a tower level in all planes? | ☐ | ☐ |
| - Is the tower built on firm and stable ground? | ☐ | ☐ |
| - Are stabilisers fitted and are they the correct size for the height of the tower? | ☐ | ☐ |
| - Check that the feet are fully in contact with the ground, and wing nuts are tight. | ☐ | ☐ |
| - Check that the foot of the stabilisers are positioned to form a squire. | ☐ | ☐ |
| - Is the bracing pattern used, in accordance with the manufacturer’s instructions? | ☐ | ☐ |
| - Check that all the hooks on the braces are fully engaged. | ☐ | ☐ |
| - Check that all the handrails and mid guardrails are fitted in the correct positions. | ☐ | ☐ |
| - Check that the interlocking devise, locking frames together are engaged. | ☐ | ☐ |
| - Check that all platforms are in the correct position on the tower. | ☐ | ☐ |
| - Check that the trap door opens to the outboard side of the tower. | ☐ | ☐ |
| - Check that, if the tower is single width that all platforms have trap doors. | ☐ | ☐ |
| - If wind locks are fitted to platform, check they are engaged. | ☐ | ☐ |
| - Are toe boards fitted to the working platform, or any platform with gear stowed? | ☐ | ☐ |
| - If the tower has been tied in check that the method is adequate and at the correct intervals in accordance with the MIM. | ☐ | ☐ |

| Signature of inspector |  |  |  |
| --- | --- | --- | --- |
| Name in block capitals |  | Date |  |

# Task 11: Safe isolation procedure

Identify the steps and equipment used for the correct safe isolation of electrical appliances and circuits.

| Step | Description |
| --- | --- |
| 1 |  |
| 2 |  |
| 3 |  |
| 4 |  |
| 5 |  |
| 6 |  |
| 7 |  |

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 12: Measuring and cutting

To use a tape measure accurately you have to ensure you are reading the correct units. In plumbing we use metric units, most commonly the millimetre.

You are required to select the following diameters of pipe and cut the lengths in the table below. The diameter is the measurement from one side to the other across the centre.

| Type | Diameter | Length to cut | Achieved (Y/N) |
| --- | --- | --- | --- |
| Copper | 15mm | 100mm |  |
| Copper | 15mm | 125mm |  |
| Copper | 22mm | 150mm |  |
| Copper | 22mm | 110mm |  |
| Plastic | 32mm | 120mm |  |
| Plastic | 40mm | 170mm |  |
| Plastic | 15mm | 130mm |  |
| Plastic | 22mm | 180mm |  |
| Steel | 15mm | 175mm |  |
| Steel | 20mm | 195mm |  |

# Task 13: Fittings

List the sizes of Copper Pipe

Identify the fittings and purpose:

| Fitting | Description | Purpose |
| --- | --- | --- |

List the sizes of Steel Pipe

Identify the fittings and purpose:

| Fitting | Description | Purpose |
| --- | --- | --- |

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 14: X and Z Dimensions

Working out the X/Z Dimensions of a fitting will allow you to measure and cut a piece of copper/steel to the correct size when working from a workshop drawing (Centre to Centre measurements)

Describe an X dimension-

Describe a Z dimension-

# Task 15: Fixings

Mark a horizontal level and fix the clips as shown below into a timber surface:

Mark a horizontal level and fix the clips as shown below into a brick or block surface:

Attach the two back plate elbows to a brick or block surface:

What tools and fixings are required to complete the task?

What PPE is required to carry out the task safely?

Learner reflection

| Do you feel confident about this topic? | Yes | I would like more guidance |
| --- | --- | --- |

# Task 16: Decommissioning

Decommissioning is the process of taking the system safely ‘out of action’, this may be either temporarily or permanently.

Temporary decommission: The process of temporarily taking a system ‘out of action’ to carry out additional work to the system, to undertake maintenance or as a result of the system not being used.

Permanently decommission: The process of permanently taking a system ‘out of action’ and removing the installation

Procedure for decommissioning systems:

- notify relevant person.

- isolate Gas/electricity supply to the system as appropriate.

- isolate water supply.

- apply warning notices and signs.

- drain system to a suitable location.

- appropriately dispose of contents and any additives.

- continuity bonding as required.

- temporary capping of pipework sections as required.

- notify building users.

- alternative source of heat or supplies as required.

Whilst working through this training manual, once the installations have been completed, checked, and verified by the customer (trainer).

You must:

- Decommission in a safe manner ensuring safe isolation.

- Ensure the workspace is made good, including filling, sanding and painting any holes or damage to the building fabric.

Following dismantling, consideration must be given to sustainability and recycling.

Notes for decommissioning:

# Task 17: Copper compression

You should now complete the frame below using compression fittings. Once complete you should then test to at least 1.5bar for 3 minutes.

X Dimensions

Materials list:

What tools are required to complete the task?

What PPE is required to carry out the task safely?

| Formative Feedback/Development points |  | Trainer to tick |
| --- | --- | --- |
| Please develop and work on the following elements: | Criteria |  |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly | ☐ |
| Pipe jointing | - Pipe and fittings are free from tool and vice marks - Malleable iron fittings show no more than 1 ½ threads | ☐ |
| Ensuring work meets industry requirements | - Completed pipework must be leak free | ☐ |
| Health and safety | - Health and safety requirements must be observed at all times | ☐ |

| Behaviours demonstrated during this task Trainer to tick |  |
| --- | --- |
| Dependable and responsible | ☐ |
| Enthusiasm and positive attitude | ☐ |
| Quality focus | ☐ |
| Willingness to learn | ☐ |
| Work with others | ☐ |
| Sustainable working | ☐ |

# Task 18: Copper soldering

You are required to fabricate the frame shown below, using 15mm copper pipe. Use end feed fittings.

| Material type (description) | Quantity |
| --- | --- |

What tools are required to complete the task?

What PPE is required to carry out the task safely?

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly | ☐ |

| Behaviours demonstrated during this task | Trainer to tick |
| --- | --- |
| Dependable and responsible | ☐ |
| Enthusiasm and positive attitude | ☐ |
| Quality focus | ☐ |
| Willingness to learn | ☐ |
| Work with others | ☐ |
| Sustainable working | ☐ |

# Task 19: Copper bending

Complete the task by using the bends pictured below’ 15mm copper tube. Remember to allow for pipe gain.

How much tube is required to form this bend?

What angle did you use to form the offset?

Recreate this bend.

Recreate this bend.

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Pipe jointing | - Pipe and fittings are free from tool and vice marks | ☐ |
| Pipe bending | - Pipe bends must be free from ripples, throating or excessive distortion | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

| Behaviours demonstrated during this task | Trainer to tick |
| --- | --- |
| Dependable and responsible | ☐ |
| Enthusiasm and positive attitude | ☐ |
| Quality focus | ☐ |
| Willingness to learn | ☐ |
| Work with others | ☐ |
| Sustainable working | ☐ |

# Task 20: Copper frame

You should now complete the frame below using compression fittings. Once complete, you should then test to at least 1.5bar for 3 minutes.

| Material type (description) | Quantity |
| --- | --- |

| Tool list – list the tools required to complete the work task |  |
| --- | --- |

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly | ☐ |
| Pipe jointing | - Soldered joints must be free from excessive solder and residual flux - Pipe and fittings are free from tool and vice marks | ☐ |
| Pipe bending | - Pipe bends must be free from ripples, throating or excessive distortion | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Ensuring work meets industry requirements | - Completed pipework must be leak free | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

| Behaviours demonstrated during this task | Trainer to tick |
| --- | --- |
| Dependable and responsible | ☐ |
| Enthusiasm and positive attitude | ☐ |
| Quality focus | ☐ |
| Willingness to learn | ☐ |
| Work with others | ☐ |
| Sustainable working | ☐ |

# Task 21: Plastic push-fit

List the fittings required to form the frame pictured below using push-fit pressure plastic pipework and note the X- dimensions then pressure test to 1.5 bar for 3 minutes.

Assemble the frame on the diagram below.

| Fitting Type | Quantity | X- Dimensions |
| --- | --- | --- |

What tools are required to complete the task?

What PPE is required to carry out the task safely?

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly |  |
| Pipe jointing | - Pipe and fittings are free from tool and vice marks | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Ensuring work meets industry requirements | - Completed pipework must be leak free | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

Learner Reflection

Give details of what you feel went well and identifying any areas for improvement.

# Task 22: Steel bending

Form the 90º bend pictured below in 15mm low carbon steel (LCS) pipe. How much pipe is required to form this bend? Also, show how much the pipe gains when it is bent to 90°.

Form the 45º bend pictured below in 20mm LCS pipe. How much pipe is required to form this bend?

List the tools and P.P.E. that you used to complete this task.

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Pipe bending | - Pipe bends must be free from ripples, throating or excessive distortion | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

# Task 23: Steel jointing

Using the 90º bend you formed in the previous task, measure the Z-dimensions of the fittings, calculate the pipe lengths required and make the frame pictured below:

| Fitting Name | Z – Dimension 1 | Z – Dimension 2 |
| --- | --- | --- |

List the tools and P.P.E. that you used to complete this task.

Which techniques did you use to make this frame?

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly | ☐ |
| Pipe jointing | - Soldered joints must be free from excessive solder and residual flux - Pipe and fittings are free from tool and vice marks - Malleable iron fittings show no more than 1 ½ threads | ☐ |
| Pipe bending | - Pipe bends must be free from ripples, throating or excessive distortion | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Ensuring work meets industry requirements | - Completed pipework must be leak free | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

Learner Reflection

Give details of what you feel went well and identifying any areas for improvement.

# Task 24: Combined frame

You are required to fabricate the combined frame and then test it to 1.5 bar for 3 minutes.

| Material type (description) | Quantity |
| --- | --- |

| Tool list – list the tools required to complete the work task |  |
| --- | --- |

| Please develop and work on the following elements: | Criteria | Trainer to tick |
| --- | --- | --- |
| Measurement | - +/- 2mm of the dimensions on the drawing | ☐ |
| Marking out | - +/- 2mm of the dimensions on the drawing - Marked out in pencil - Spirit level used | ☐ |
| Clipping | - Select appropriate pipework clips for use and space them correctly | ☐ |
| Pipe jointing | - Soldered joints must be free from excessive solder and residual flux - Pipe and fittings are free from tool and vice marks - Malleable iron fittings show no more than 1 ½ threads | ☐ |
| Pipe bending | - Pipe bends must be free from ripples, throating or excessive distortion | ☐ |
| Presentation of work | - The task is completed according to the brief, with all components correctly oriented. | ☐ |
| Ensuring work meets industry requirements | - Completed pipework must be leak free | ☐ |
| Health & safety | - Health and safety requirements must be observed at all times | ☐ |

| Behaviours demonstrated during this task | Trainer to tick |
| --- | --- |
| Dependable and responsible | ☐ |
| Enthusiasm and positive attitude | ☐ |
| Quality focus | ☐ |
| Willingness to learn | ☐ |
| Work with others | ☐ |
| Sustainable working | ☐ |

# Task 25: Electrical tools

Identify the tool and its use:

| Tools/Equipment | Name/Use |
| --- | --- |

What is the safety feature of electrical tools?

# Task 26: Fittings and jointing materials identification

Your trainer will now supply you with a range of fittings and jointing materials, you should identify the suitability to be used on a gas pipework and record it in the table below.

|  | Identification of fitting | Appropriate for gas? |
| --- | --- | --- |
| 1. |  |  |
| 2. |  |  |
| 3. |  |  |
| 4. |  |  |
| 5. |  |  |
| 6. |  |  |
| 7. |  |  |
| 8. |  |  |
| 9. |  |  |
| 10. |  |  |
| 11. |  |  |
| 12. |  |  |

# Task 27: Termination of BS1363 plug top

Aim:

To terminate BS1363 plug top using 1.5mm2 3 core flexible cable.

Objective:

Label the plug top using coloured pencils.

- Obtain materials and tools

- Terminate 1.5mm2 3 core flexible cable into plug top

- Secure cover and inform trainer of completed task

- Clean & Tidy work area

| Marking scheme |  |
| --- | --- |
| 1 | Correct polarity of plug top |
| 2 | Termination secure |
| 3 | Cord grip secure |
| 4 | Front cover secure |
| Trainer feedback |  |
| Is the installation complete to a satisfactory industrial standard |  |

# Task 28: Operating a U gauge and digital manometer

Your trainer will provide you with an empty U gauge and digital manometer together with a section of pipework and appropriate hand air pump required to perform this task. Complete all tasks below:

| Item | Task | Check |
| --- | --- | --- |
| 1 | Identify and correctly fill/ calibrate U gauge |  |
| 2 | Select appropriate tools for the task and inspect for safety |  |
| 3 | Check hoses for leaks |  |
| 4 | Connect hose to test point |  |
| 5 | Charge U gauge to 10mbar and 20mbar accurately |  |
| 6 | Remove U gauge and check for leaks |  |
| 7 | Select and calibrate digital manometer |  |
| 8 | Check hoses for leaks |  |
| 9 | Connect hose to test point |  |
| 10 | Charge digital manometer to 10mbar and 20mbar accurately |  |
| 11 | Remove manometer and check test point for leaks |  |
| 12 | Complete task in a safe working area |  |

Identify how many mbar is displayed below:

# Task 29: Gas meters and enclosures

Use your knowledge of gas meters to identify the meters in the workshop area or use the images provided.

Using the examples given to you by your tutor, identify the following 6 types of Gas meter. You should also state whether they are imperial or metric.

1.

2.

3.

4.

5.

6.

# Task 30: Let-by testing and tightness testing – low pressure

You will be allocated a training bay by your trainer. The task is as follows:

Carry out a let-by and tightness test. What are the results of this test?

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

| Installation |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| How many appliances are fitted? |  |  |  |  |  | Appliance types (if applicable) |  |  |  |  |  |  |
| Let-by test |  |  |  |  |  |  |  |  |  |  |  |  |
| Let-by pressure |  |  | mbar |  |  |  |  | Duration (minutes) |  |  |  |  |
| Is the ECV letting by? |  |  | If yes, record actions taken: |  |  |  |  |  |  |  |  |  |
| Yes | No |  |  |  |  |  |  |  |  |  |  |  |
| Tightness test |  |  |  |  |  |  |  |  |  |  |  |  |
| Stabilisation period pressure |  |  |  | mbar |  |  | Duration (minutes |  |  |  |  |  |
| Tightness test pressure |  |  |  | mbar |  |  | Duration (minutes) |  |  |  |  |  |
| Explain why we test at this pressure: |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum permissible drop |  |  |  |  | mbar |  | Is the installation gas tight? If no, state why and the actions required |  |  |  | Yes | No |
| What is the operating pressure in your bay? |  | What is the correct operating pressure of the meter regulator? |  |  |  |  | Actions required: |  |  |  |  |  |
| mbar |  | mbar |  |  |  |  |  |  |  |  |  |  |

# Task 31: Let-by testing and tightness testing – medium pressure

You will be allocated a training bay by your trainer. The task is as follows:

Carry out a let by and tightness test. What are the results of this test?

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

| Installation |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| How many appliances are fitted? |  |  |  |  |  | Appliance types (if applicable) |  |  |  |  |  |  |
| Let-by test |  |  |  |  |  |  |  |  |  |  |  |  |
| Let-by pressure |  |  | mbar |  |  |  |  | Duration (minutes) |  |  |  |  |
| Is the ECV letting by? |  |  | If yes, record actions taken: |  |  |  |  |  |  |  |  |  |
| Yes | No |  |  |  |  |  |  |  |  |  |  |  |
| Tightness test |  |  |  |  |  |  |  |  |  |  |  |  |
| Stabilisation period pressure |  |  |  | mbar |  |  | Duration (minutes) |  |  |  |  |  |
| Tightness test pressure |  |  |  | mbar |  |  | Duration (minutes) |  |  |  |  |  |
| Explain why we test at this pressure: |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum permissible drop |  |  |  |  | mbar |  | Is the installation gas tight? If no, state why and the actions required |  |  |  | Yes | No |
| What is the operating pressure in your bay? |  | What is the correct operating pressure of the meter regulator? |  |  |  |  | Actions required: |  |  |  |  |  |
| mbar |  | mbar |  |  |  |  |  |  |  |  |  |  |

# Task 32: Purging

You will be allocated a training bay by your trainer. The task is as follows:

Carry out the purging process.

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

| Installation |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| How many appliances are fitted? |  |  |  | Appliance types (if applicable) |  |  |  |  |  |  |  |
| Volumes |  |  |  |  |  |  |  |  |  |  |  |
| Meter volume (IVm) |  |  |  |  |  |  |  |  | IVm | = | m3 |
| Pipework volume (IVp) |  |  |  |  | m of 35mm copper |  |  |  | x 0.00084 | = | m3 |
|  |  |  |  |  | m of 28mm copper |  |  |  | x 0.00054 | = | m3 |
|  |  |  |  |  | m of 22mm copper |  |  |  | x 0.00032 | = | m3 |
|  |  |  |  |  | m of 15mm copper |  |  |  | x 0.00014 | = | m3 |
|  |  |  |  |  |  |  |  |  | IVp | = | m3 |
| Fittings volume (IVf) = IVp x 0.1 |  |  |  |  |  |  |  |  | IVf | = | m3 |
| Total volume (IVt) |  |  |  |  |  |  |  |  |  |  |  |
| IVm + IVp + IVf = IVt |  | + |  |  |  | + |  |  | IVt | = | m3 |
| Purge volume (PV) |  |  |  |  |  |  |  |  |  |  |  |
| IVt x 1.5 = PV |  |  |  |  |  |  |  |  | PV | = | m3 |

| Purge volume for the system | m3 |
| --- | --- |
| Purge method to be used |  |

Answer the following questions:

Give a brief description of the gas network from the beach to the building:

What are the operating pressure ranges of the following:

- Low pressure

- Medium pressure

- Intermediate pressure

- High pressure

Describe the different types of gases used to supply gas appliances in domestic dwellings:

What are the requirements when issuing testing and purging certificates?

What is the correct action to take when a non-commissioned appliance is identified?

What is the correct action to take if pipework and appliances are not commissioned when the gas supply to the property is re-established?

State the purge volume for an installation containing a U6 mater, 3m of 28mm pipe and 5m of 22mm pipe.

# Task 33: The installation pipework

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

You will be allocated a training bay by your trainer. The tasks are as follows:

Visually inspect the installation pipework and record any faults.

| Is the ECV installed correctly? |  |  | Yes |  |  | No |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| If no, state why not: |  |  |  |  |  |  |  |  |  |  |
| Is the installation pipework installed correctly? |  |  | Yes |  |  | No |  |  |  |  |
| If no, state why not: |  |  |  |  |  |  |  |  |  |  |
| Record and describe briefly one (1) AR/ID situation which may exist with the installation. Identify which notice and labels should be used and detail the correct procedure to be followed to make the installation safe. |  |  |  |  |  |  |  |  |  |  |

Extend the installation pipework to an appliance in the bay allocated to suit a new position as indicated by your trainer. Your installation may include copper pipe, low carbon steel tube and/or Corrugated Stainless Steel Tube (CSST).

| Record findings before pipework alteration |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Let-by test |  |  |  |  |  |  |  |  |
| Let-by pressure. |  | mbar |  |  | Duration (minutes) |  |  |  |
| Is the ECV letting by? |  | If yes, record actions you would take: |  |  |  |  |  |  |
| Yes | No |  |  |  |  |  |  |  |
| Tightness test |  |  |  |  |  |  |  |  |
| Stabilisation period pressure |  |  | mbar | Duration (minutes) |  |  |  |  |
| Tightness test pressure |  |  | mbar | Duration (minutes) |  |  |  |  |
| Explain why we test at this pressure: |  |  |  |  |  |  |  |  |
| Maximum permissible drop |  | mbar |  | Is the installation gas tight? If no, state why and the actions required |  |  | YES | NO |
| What is the operating pressure in your bay? |  | What is the correct operating pressure of the system? |  | Actions required: |  |  |  |  |
| mbar |  | mbar |  |  |  |  |  |  |

| Photographs |  |
| --- | --- |
| Installation BEFORE alteration | Installation AFTER alteration |

Give a brief description of the work completed including the type and size of pipework and fittings used:

| Record findings after pipework alteration |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Let-by test |  |  |  |  |  |  |  |  |  |
| Let-by pressure. |  |  | mbar |  |  | Duration (minutes) |  |  |  |
| Is the ECV letting by? |  |  | If yes, record actions you would take: |  |  |  |  |  |  |
| Yes |  | No |  |  |  |  |  |  |  |
| Tightness test |  |  |  |  |  |  |  |  |  |
| Stabilisation period pressure |  |  |  | mbar | Duration (minutes) |  |  |  |  |
| Tightness test pressure |  |  |  | mbar | Duration (minutes) |  |  |  |  |
| Maximum permissible drop |  |  | mbar |  | Is the installation gas tight? If no, state why and the actions required |  | Yes | No |  |
|  | Actions required: |  |  |  |  |  |  |  |  |

Check the standing pressure and the operating pressure at the meter.

| From the relevant pressure test point, record the following |  |  |
| --- | --- | --- |
| Standing pressure: |  | mbar |
| Operating pressure at the meter: |  | mbar |
| Operating pressure at the appliance: |  | mbar |
| What is the maximum permissible pressure drop between the meter and the appliance? |  | mbar |

Answer the following questions:

For the purposes of these questions, the Gas Safety (Installation and Use) Regulations will be abbreviated to ‘GSIUR’.

Produce a plan of the installation you have just altered showing the positioning and protection of pipework and fixing methods.

British Standard BS6891:2019 specifies the design, materials and methods of installing gas pipework, but what is the maximum size and pressure it refers to?

Describe how to take measurements and record details for fabrication of pipework off-site.

Using the method specified in the nominated textbooks, calculate the pipe sizes for the following installation.

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pipe section | Gross heat input | Gas flow rate (kW x 0.09) | Actual pipe length | Allowance for fittings |  | Equivalent length (4+6) | Pipe dia. (chart) | pressure loss per m (mbar) | Pressure loss |
|  |  |  |  | No. and type in section | Length |  |  |  |  |
|  | Kw gross | M3/h | m |  | m | m | mm | mbar | mbar |

Name four types of materials for gas pipework installations.

1.

2.

3.

4.

Explain how the above pipe materials can be bent.

‘Tracpipe’ corrugated stainless steel tubing conforms to the BS7838 bend test. What does the bend test stipulate?

What precautions must be exercised when making new connections on existing gas installations?

Explain how to set gas meter regulators.

What is the requirement where a pipe passes through a solid wall?

Explain how to confirm that the gas supply and earthing system are adequate for the installation of the new gas system and components or, for extending the system or adding components to system.

Which type of pipework can be used within a protected structure but not used within a protected shaft?

Where should the main equipotential bonding be connected to the installation pipework?

According to GSIUR Regulation 18, main equipotential bonding is most commonly required on which two types of installations?

When should a temporary continuity bond be used?

True or false? Temporary continuity bonds can be left permanently in place.

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 34: Installing a boiler

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Complete the installation a central heating boiler in a position as indicated by your trainer. Commission the appliance in accordance with the manufacturer’s instructions leaving the appliance in full working order.

| Complete the following commissioning checklist |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler make |  |  |  | Model number/name |  |  |  |  |  |  |  |  |  |  |  |  |
| Appliance classification: Type A – flueless / Type B – Open flue / Type C – Room sealed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Natural draught |  |  |  |  | Fanned draught |  |  |  |  |  |  |  |  |  |  |  |
| Appliance location satisfactory? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Ventilation provision satisfactory? |  |  |  |  |  |  |  | N/A |  |  |  | Yes |  |  | No |  |
| Flue/chimney visual check satisfactory? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flue flow test satisfactory? |  |  |  |  |  |  | N/A |  |  |  |  | Yes |  |  | No |  |
| Gas rate: |  |  |  |  |  |  |  |  |  |  |  | m³/h |  |  |  |  |
| Gas rate satisfactory? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Heat input |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |
| Heat input satisfactory? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Burner pressure |  |  |  |  |  |  |  |  |  |  |  | mbar |  |  |  |  |
| Burner pressure satisfactory? |  |  |  |  |  |  |  | N/A |  |  |  | Yes |  |  | No |  |
| Flame picture satisfactory? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flue integrity readings (as required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CO2 |  |  | O2 |  |  | CO |  |  |  |  | CO/CO2 |  |  |  |  |  |
| N/A |  |  | % |  |  | ppm |  |  |  |  | N/A |  |  |  |  |  |
| Combustion performance readings (as required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CO2 |  | O2 |  |  | CO |  |  |  |  | CO/CO2 |  |  |  |  |  |  |
| INITIAL % |  | INITIAL % |  |  | INITIAL ppm |  |  |  |  | INITIAL |  |  |  |  |  |  |
| FINAL % |  | FINAL % |  |  | FINAL ppm |  |  |  |  | FINAL |  |  |  |  |  |  |
| Ignition system operating? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flame failure device/flame rectification operating? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Thermostats operating? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Spillage test satisfactory? (if applicable) |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Finished installation gas tight? |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Record any observations/faults/detail of any adjustments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Answer the following questions:

For the purposes of these questions, the Gas Safety (Installation and Use) Regulations will be abbreviated to ‘GSIUR’.

What information does the appliance data plate contain?

What is the purpose of gas water heating and central heating appliances in dwellings?

State the typical flue gas temperature ranges of a condensing boiler.

State the minimum gradient and direction of a condensing boiler flue.

Which pipe materials are recommended for condensate removal?

State the minimum gradient of a condensate pipe.

List suitable discharge points for the condensate pipework.

What are the methods of determining and/or setting gas appliance operating pressures?

Explain the working principles of central heating appliances.

Explain how central heating controls operate heating systems.

Explain how to determine the gas rates at appliances

What is the procedure when an incorrect pressure reading is noted on a gas system?

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 35: Gas rating

We Gas rate to confirm that an appliance is operating correctly and in accordance with Manufacturer’s Instructions.

How is the Gas Rate measured on an Imperial meter?

We need to measure the quantity of gas flowing into the appliance.

An Imperial Meter (U6)

We are interested in the meter test dial only.

One full revolution = 1ft³ of gas has flowed

3600 = Seconds in an hour

1040 = calorific value in btu per cubic foot (ft³)

3412 = You use this number to divide btu/hr in kW

The formula =

This will give you your answer in BTU’s/hour – you should now convert it to KW’s by dividing it by 3412.

A Metric Meter (E6)

- Write meter reading down before time test.

- Take note of meter reading after time test.

- Record the amount of time test has taken minimum 2 minutes till full revolution of last digit.

3600 = Seconds in an hour

10.76 = energy in a cubic meter of gas m³

The formula =

Your tutor will now set you up on at least one of each of the following appliances and you are required to complete a gas rate and record it for each appliance also stating whether the result is satisfactory using the Manufacturer’s Instructions and the data plate.

| Appliance (Including make & model) | Gas Rate | Satisfactory? |
| --- | --- | --- |
| Boiler |  |  |
| Fire |  |  |
| Boiler |  |  |
| Water Heater |  |  |

You should now use calculate the Gas rate for 2 appliances fitted with smart meters, record this and state whether they are satisfactory or not.

| Appliance (Including make & model) | Gas Rate | Satisfactory? |
| --- | --- | --- |

Answer the following questions:

What is the purpose of gas rating?

What are the dangers of an appliance burning too much gas?

A metric meter measures what volume?

An Imperial meter measures what volume?

A gas boiler uses 0.049 m³ in 120 seconds what is the gross kW rating?

A gas boiler uses 0.079 m³ in 120 seconds what is its net kW rating?

A boiler is gas rated on an imperial meter one revolution takes 66 seconds what is the gross kW rating?

A boiler is gas rated on an imperial meter one revolution takes 29 seconds what is the net kW rating?

# Task 36: Gas flow and pressure loss

You are required to set up a Metered Installation with a long pipe run with a minimum of 3 connected burners and test points at various points (Including prior to the burners).

Following the steps below, you should relate back to the appliance Manufacturer Instructions to see if they are acceptable.

Procedure:

- Set Up the Installation

  - Assemble a metered installation with a pipe run supplying at least 3 gas appliances

- Initial Checks

  - Perform a tightness test to confirm there are no leaks.

  - Confirm all burners are leak free

- Set Regulator Pressure to 21 mbar

  - Adjust the meter regulator to 21 mbar using the screwdriver and U-tube gauge.

  - Test each burner individually and all burners together.

  - Record the burner pressures at each test point.

|  | Appliance Type, Make and Model | Burner pressure |
| --- | --- | --- |
| Appliance 1 |  |  |
| Appliance 2 |  |  |
| Appliance 3 |  |  |
| All Appliances |  |  |

- Reset Regulator Pressure to 16 mbar

  - Adjust the meter regulator to 16 mbar.

  - Repeat the same sequence of pressure tests:

    - Each burner individually.

    - Both burners operating together.

  - Record all readings.

|  | Appliance Type, Make and Model | Burner pressure |
| --- | --- | --- |
| Appliance 1 |  |  |
| Appliance 2 |  |  |
| Appliance 3 |  |  |
| All Appliances |  |  |

- Reset Regulator Pressure to 12 mbar

  - Adjust the regulator to 12 mbar.

  - Repeat the pressure tests as above.

  - Record final readings at all test points.

|  | Appliance Type, Make and Model | Burner pressure |
| --- | --- | --- |
| Appliance 1 |  |  |
| Appliance 2 |  |  |
| Appliance 3 |  |  |
| All Appliances |  |  |

- Shut Down and Record Results

  - Safely turn off all gas supply and burners.

  - Record all data in the test sheet.

  - Return the system to 21 mbar when complete.

# Task 37: Pressure regulators

Your trainer will now give you the following type of regulators:

- Constant Pressure

- Simple Pressure

- Zero Pressure

Part 1 – Identification and Examination

- Examine each regulator (constant pressure, simple, and zero pressure) and record the following details for each one. Once complete you should discuss the intended application.

  - Connection size and thread type

  - Inlet and outlet pressure range

  - Direction of flow

  - Breather hole position

  - Impulse port position (if applicable)

  - Lock-up pressure specification (from manufacturer data)

|  | Constant | Simple | Zero |
| --- | --- | --- | --- |
| Connection size and thread type |  |  |  |
| Inlet and outlet pressure range |  |  |  |
| Direction of flow |  |  |  |
| Breather hole position |  |  |  |
| Impulse port position (if applicable) |  |  |  |
| Lock-up pressure specification (from manufacturer data) |  |  |  |

Part 2 – Setting Up Regulators

- Install each regulator in turn onto a training meter setup or appliance in accordance with industry best practices and manufacturer instructions.

- Carry out a tightness test before supplying gas.

- Adjust each regulator to the required outlet pressure using a manometer.

- Record:

  - Inlet pressure

  - Outlet pressure

  - Lock-up pressure

  - Pressure stability under flow conditions

- Check for any gas escape around joints and the breather hole.

Part 3 – Fault Simulation and Analysis

- The trainer will introduce one or more faults into the system:

  - Blocked or sealed breather hole

  - Incorrect spring tension

  - Restricted or damaged diaphragm

  - Low inlet pressure (meter supply issue)

  - Misconnected impulse line

- Identify the fault through observation, testing, and reasoning.

- Record:

  - Observed appliance performance (e.g., flame instability, failure to light, yellow tipping, etc.)

  - Measured pressure values at various test points

  - Diagnosis of the fault cause and corrective action required.

- Restore the system to correct operation after approval from the trainer.

Part 4 – Discussion and Evaluation

- Explain to your trainer how incorrect regulator performance can:

  - Affect appliance combustion quality

  - Lead to low-pressure faults or unsafe operation

  - Impact meter performance and overall system balance

- Discuss the importance of lock-up testing and how this ensures regulator safety.

- Compare the operating characteristics of constant pressure, simple, and zero pressure regulators.

# Task 38: Servicing a boiler

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Service the central heating boiler in accordance with the manufacturer’s instructions leaving the appliance in full working order.

| Complete the following servicing checklist |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler make |  |  |  |  |  | Model number/name |  |  |  |  |  |  |  |  |  |  |  |
| Appliance classification: Type A – flueless / Type B – Open flue / Type C – Room sealed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Natural draught |  |  |  |  | Fanned draught |  |  |  |  |  |  |  |  |  |  |  |  |
| Appliance location satisfactory? |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |  |  |
| Ventilation provision satisfactory? |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |  |  |
| What is the visual condition of the appliance? (tick as appropriate) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Excellent |  |  | Good |  | Satisfactory |  |  |  |  |  | Poor |  |  |  |  |  |  |
| Record any observations/faults (i.e. casing condition, fixings, case seal etc.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Flue/chimney visual check satisfactory? |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  |  | No |  |
| Record any observations/faults: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Servicing procedure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Burner removed and cleaned? |  | Yes |  | No |  | Pilot assembly removed and inspected/cleaned? |  |  |  |  |  |  |  | Yes |  |  |  | No |  |  |  |
| Burner injector inspected and cleaned? |  | Yes |  | No |  | Flame rectification and spark electrodes in good condition? |  |  |  |  |  |  |  | Yes |  |  |  | No |  |  |  |
| Heat exchanger cleaned? |  | Yes |  | No |  | Combustion chamber free of debris? |  |  |  |  |  |  |  | Yes |  |  |  | No |  |  |  |
| Flue ways Inspected and cleaned? |  | Yes |  | No |  | Fan assembly removed and cleaned? (if applicable) |  |  |  |  |  |  |  | Yes |  |  |  | No |  |  |  |
| Has the condensate trap and pipework been inspected, checked and cleaned? |  | Yes |  | No |  | N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Post servicing tests and procedures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Flue flow test satisfactory? |  |  |  |  |  |  |  |  |  | N/A |  |  |  | Yes |  |  |  |  | No |  |  |
| Burner pressure: |  |  |  |  |  |  |  |  |  |  |  |  |  | mbar |  |  |  |  |  |  |  |
| Gas rate: |  |  |  |  |  |  |  |  |  |  |  |  |  | M3/h |  |  |  |  |  |  |  |
| Heat input: |  |  |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |  |  |  |
| Pressure/heat input/gas rate satisfactory: |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Flame picture satisfactory? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Combustion performance readings (as required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CO2 | O2 |  |  |  |  | CO |  |  |  |  |  |  | CO/CO2 |  |  |  |  |  |  |  |  |
| INITIAL % | INITIAL % |  |  |  |  | INITIAL ppm |  |  |  |  |  |  | INITIAL |  |  |  |  |  |  |  |  |
| FINAL % | FINAL % |  |  |  |  | FINAL ppm |  |  |  |  |  |  | FINAL |  |  |  |  |  |  |  |  |
| Ignition system operating? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Flame failure device/flame rectification operating? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Thermostats operating? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Spillage test satisfactory? (if applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Finished installation gas tight? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Record any observations/faults, including details of any rectification work carried out: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| What type of system is fitted? |  |  |  | Sealed |  |  |  |  |  |  | Vented |  |  |  |  |  |  |  |  |  |  |
| Filling loop removed? (for Water Regulations compliance) |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| System pressure or water level in the F & E cistern checked? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| External controls checked for safe operation? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |
| Appliance safe to use? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |

| Learner signature: | Trainer signature: |
| --- | --- |

Your trainer will provide various types of gas burners (e.g., simplex, duplex, etc.) installed on a simple pipework rig. (Ensuring test points are available prior to the burner).

Instructions

The learner should examine each burner and answer the following questions:

- What is the name of the manufacturer and the type of burner?

- What is the injector size (indicated by letter or number) and type (single or multi-hole)?

- What is the aeration size? Is it fixed or adjustable, and how is it adjusted?

- Is the burner simplex or duplex?

- How is flame retention achieved on this burner?

- How are the burner ports arranged? (Provide sketches or diagrams to illustrate the arrangement).

Practical Exercise:

Where possible, the learner should:

- Light the burners.

- Adjust the gas and/or air supply.

- Observe and analyse the varying flame pictures.

Appliance Analysis:

- Move on to appliances and determine the burner and injector specifications, then answer the following questions:

a. What is the make and model of the appliance?

b. What is the burner type and injector size/type?

Identifying Combustion Faults:

- The learner should inspect the burners and identify any faults based on the flame appearance.

Flame Temperature Analysis

- Using a Bunsen burner, instruct the learner to measure the flame temperatures at different air port settings (fully open, mid-position, and fully closed). The following temperature readings should be recorded:

a.

b.

c.

d.

- The learner should complete a chart documenting the temperature variations at each air port setting.

# Task 39: Flues and chimneys

This paperwork is to be completed in full as the task progresses. Incomplete paperwork will result in you being asked to start again from the beginning of the task. If you are in any doubt, ask your trainer.

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Visually inspect and test a flue for flue flow and spillage.

| Boiler manufacturer |  |  |  |  |  | Model number |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Heat input |  |  | kW |  |  | Heat output |  |  | kW |  |  |
| Flue type | Open flue |  |  | Room sealed |  | Flue draught | Natural |  |  | Fanned |  |
| Case pressure |  | Positive |  |  | Negative |  |  | Atmospheric |  |  |  |

| Visual chimney inspection |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type of flue/chimney |  |  |  |  |  |  |  |  |  |  |  |
| Visual Inspection of the chimney/flue |  |  |  |  |  | Pass |  |  | Fail |  |  |
| Visual inspection of the appliance |  |  |  |  |  | Case seal integrity |  |  |  |  |  |
| Pass |  |  |  | Fail |  | Pass |  |  |  | Fail |  |
| If any of these tests are unsatisfactory, please indicate the reasons in the space below |  |  |  |  |  |  |  |  |  |  |  |
| Flue flow and spillage tests |  |  |  |  |  |  |  |  |  |  |  |
| Type of flue/chimney |  |  |  |  |  |  |  |  |  |  |  |
| Flue flow test |  |  |  |  |  | Spillage test |  |  |  |  |  |
| Pass |  |  |  | Fail |  | Pass |  |  |  | Fail |  |
| If either of these tests are unsatisfactory, please indicate the reasons in the space below |  |  |  |  |  |  |  |  |  |  |  |

# Task 40: Flues and chimneys part 2

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Inspect the following open flues and detail any installation faults found.

| Flue types |  |
| --- | --- |
| Twin wall chimney | Brick built chimney |
| Precast flue system | Cement based flue |

Answer the following questions:

For the purposes of these questions, the Gas Safety (Installation and Use) Regulations will be abbreviated to ‘GSIUR’.

- Give a brief description of carbon monoxide.

- Give one method of testing the reliability of carbon monoxide detectors.

- State the British Standard for carbon monoxide detectors.

- On the room drawing below, indicate the correct position for the correct installation of carbon monoxide detectors.

- State five positions in a dwelling where carbon monoxide detectors should not be installed:

1.

2.

3.

4.

5.

- The British Standard gives guidance and advice about the positioning of carbon monoxide detectors. It states that if detectors cannot be fitted in every room, then priority should be given to which types of rooms?

- List the factors that can affect flue performance:

- What are the requirements for the provision of hearths used with gas appliances?

- What does Regulation 27 of the GSIUR state that a flue must be?

- What are the layout features and uses of the following chimneys/flues?

- Brick/masonry chimneys

- Pre-cast concrete flue blocks

- Flexible metal flue liners

- Twin wall insulated flue pipes

- Name the parts of an open flue.

- Describe why condensation can occur in an open flue.

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 41: Ventilation

(Your trainer will give you a choice of different vents)

Study the picture below then, using the ventilation formula provided by your trainer and the domestic gas manual, calculate the ventilation requirement for each appliance (as if it was a single appliance in that room) and record your answers. You will then be asked to choose an appropriate vent. When that task is completed, you will then calculate the vent requirements for the room with all appliances installed (multi appliance ventilation) and again choose the appropriate vent.

Room measurements width 2m, length 2m, height 2m.

Ventilation questions

- What are the ventilation requirements if only the (Open flued) boiler above is installed in the room?

- What are the ventilation requirements if only the water heater is installed in the room?

- What type of vent would you install?

- What are the ventilation requirements if only the cooker is installed in the room?

- What are the ventilation requirements if only the fire is installed in the room?

- The ventilation requirements for this room containing all appliances would be…?

- An air vent fitted in an internal room shall be fitted no higher than? Why is this?

Compartment Ventilation

What you need to do

Study the picture below, then using resources from previous pages answer the following questions.

Calculate the vent requirements for the situation above.

1. What are the vent requirements for Room 1?

2. What are the vent requirements for Room 2?

3. What are the vent requirements for Room 3?

4. What are the vent requirements for the compartment vent at high level?

5. What are the vent requirements for the compartment vent at low level?

6. Consider a room built as a single room that contain two DFE fires each with a heat input of 7.5kW, what would be the ventilation requirements for this room?

7. If the fires in the room were then exchanged for two DFE fires with a heat input of 7.5kW each, what would now be the vent requirements for this room?

# Task 42: Installing a gas multipoint water heater

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Complete the installation an instantaneous multipoint water heater in a position as indicated by your trainer. Commission the appliance in accordance with the manufacturer’s instructions leaving the appliance in full working order.

| Complete the following commissioning checklist |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water heater make |  |  | Model number/name |  |  |  |  |  |  |  |  |  |
| Appliance classification: Type A – flueless / Type B – Open flue / Type C – Room sealed |  |  |  |  |  |  |  |  |  |  |  |  |
| Natural draught |  |  |  | Fanned draught |  |  |  |  |  |  |  |  |
| Appliance location satisfactory? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Ventilation provision satisfactory? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flue/chimney visual check satisfactory? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flue flow test satisfactory? |  |  |  |  | N/A |  |  | Yes |  |  | No |  |
| Heat input: |  |  |  |  |  |  |  | kW |  |  |  |  |
| Gas rate: |  |  |  |  |  |  |  | m3/h |  |  |  |  |
| Burner pressure: |  |  |  |  |  |  |  | mbar |  |  |  |  |
| Pressure/heat input/gas rate satisfactory? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flame picture satisfactory? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Combustion performance readings (as required) |  |  |  |  |  |  |  |  |  |  |  |  |
| CO2 |  | O2 |  | CO |  |  | CO/CO2 |  |  |  |  |  |
| INITIAL % |  | INITIAL % |  | INITIAL ppm |  |  | INITIAL |  |  |  |  |  |
| FINAL % |  | FINAL % |  | FINAL ppm |  |  | FINAL |  |  |  |  |  |
| Ignition system operating? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Flame failure device/flame rectification operating? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Thermostats operating? |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Spillage test satisfactory? (if applicable) |  |  |  |  |  |  |  | Yes |  |  | No |  |
| Finished installation gas tight? |  |  |  |  |  |  |  | Yes |  |  | No |  |

| Record any observations/faults/detail of any adjustments: |  |  |
| --- | --- | --- |

| Hot water flow rate: | Litres/minute |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Hot water temperature: | OC |  |  |  |  |
| Hot water and flow rate in accordance with manufacturer’s instructions? |  | Yes |  | No |  |
| Appliance safe to use? |  | Yes |  | No |  |

| Learner signature: | Trainer signature: |
| --- | --- |

Answer the following questions:

For the purposes of these questions, the Gas Safety (Installation and Use) Regulations will be abbreviated to ‘GSIUR’.

- Produce a diagram showing how the following appliances work. You should also give a written response in the space below your diagram:

| Gas fired water heater | Combi Boiler |
| --- | --- |

- Identify the working principles of water heating appliances

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 43: Servicing a gas multipoint water heater

You will be allocated a training bay by your trainer. The task is as follows:

| Bay number |  | Meter type |  |
| --- | --- | --- | --- |

Service a gas multipoint water heater

| Complete the following servicing checklist |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water heater make: |  |  |  | Model number/name: |  |  |  |  |  |  |
| Appliance classification: Type A – flueless / Type B – Open flue / Type C – Room sealed |  |  |  |  |  |  |  |  |  |  |
| Natural draught |  |  |  | Fanned draught |  |  |  |  |  |  |
| Appliance location satisfactory? |  |  |  |  | Yes |  |  | No |  |  |
| Ventilation provision satisfactory? |  |  |  |  | Yes |  |  | No |  |  |
| What is the visual condition of the appliance? (tick as appropriate) |  |  |  |  |  |  |  |  |  |  |
| Excellent |  | Good |  | Satisfactory |  |  |  | Poor |  |  |
| Record any observations/faults (I.e. casing condition, fixings, case seal etc.): |  |  |  |  |  |  |  |  |  |  |
| Flue/chimney visual check satisfactory? |  |  |  |  | Yes |  |  | No |  |  |
| Record any observations/faults: |  |  |  |  |  |  |  |  |  |  |

| Servicing procedure (tick as required): |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Check the piezo unit, flame safety device and thermocouple, clean or replace if necessary. | Completed | N/A | Check the pilot injector and clean or replace if necessary. | Completed | N/A |
| Remove and clean the burner assembly. | Completed | N/A | Clean the lint filter. | Completed | N/A |
| Check for water soundness. Replace ‘O’ rings, sealing washers and gaskets where required. | Completed | N/A | Remove the water governor assembly complete with push rod. Replace the seals if necessary | Completed | N/A |
| Record any observations/faults: |  |  |  |  |  |

| Post servicing tests and procedures: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flue flow test satisfactory? |  |  |  |  | Yes |  |  | No |  |  |
| Heat input: |  |  |  |  | kW |  |  |  |  |  |
| Gas rate: |  |  |  |  | m3/h |  |  |  |  |  |
| Burner pressure: |  |  |  |  | mbar |  |  |  |  |  |
| Pressure/heat input/gas rate satisfactory: |  |  |  |  | Yes |  |  | No |  |  |
| Flame picture satisfactory? |  |  |  |  | Yes |  |  | No |  |  |
| Combustion performance readings (as required) |  |  |  |  |  |  |  |  |  |  |
| CO2 | O2 | CO |  |  | CO/CO2 |  |  |  |  |  |
| INITIAL % | INITIAL % | INITIAL ppm |  |  | INITIAL |  |  |  |  |  |
| FINAL % | FINAL % | FINAL ppm |  |  | FINAL |  |  |  |  |  |
| Ignition system operating? |  |  |  |  | Yes |  |  | No |  |  |
| Flame failure device/flame rectification operating? |  |  |  |  | Yes |  |  | No |  |  |
| High limit thermostat/energy cut-out operating? |  |  | N/A |  | Yes |  |  | No |  |  |
| Spillage test satisfactory? (if applicable) |  |  |  |  | Yes |  |  | No |  |  |
| Finished installation gas tight? |  |  |  |  | Yes |  |  | No |  |  |
| Record any observations/faults, including any rectification work carried out: |  |  |  |  |  |  |  |  |  |  |
| Hot water flow rate: |  |  |  |  | Litres/minute |  |  |  |  |  |
| Hot water temperature: |  |  |  |  | OC |  |  |  |  |  |
| Hot water and flow rate in accordance with manufacturer’s instructions? |  |  |  |  | Yes |  |  |  | No |  |
| Appliance safe to use? |  |  |  |  | Yes |  |  |  | No |  |

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 44: Electrical safe isolation procedure and electrical testing

You will be allocated a training bay by your trainer. The task is as follows:

Demonstrate understanding of the electrical safe isolation procedure.

| Bay number |  |  | Appliances fitted |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler type (if fitted) |  |  |  |  |  |  |  |  |
| Heat input |  | kW | Heat output |  |  | kW |  |  |
| Fuse rating |  | Amp | Switched fuse spur fitted |  | Yes |  | No |  |
| 1 | Obtained permission to carry out the work? |  |  |  | Yes |  | No |  |
| 2 | Identified the correct circuit for isolation? |  |  |  | Yes |  | No |  |
| 3 | Selected a suitable testing device? |  |  |  | Yes |  | No |  |
| 4 | Proved that the testing device is working correctly on a known proving unit? |  |  |  | Yes |  | No |  |
| 5 | Isolated the supply to be tested? |  |  |  | Yes |  | No |  |
| 6 | Secured the means of isolation using a suitable device or padlock? |  |  |  | Yes |  | No |  |
| 7 | Confirmed that the circuit is dead by testing between line (live) and earth, line and neutral and earth and neutral at the point of work? |  |  |  | Yes |  | No |  |
| 8 | Re-proved the test instrument is working correctly on a known voltage or proving unit? |  |  |  | Yes |  | No |  |
| 9 | Applied a warning label to the isolation point and inform responsible person? |  |  |  | Yes |  | No |  |

| Learner signature: | Trainer signature: |
| --- | --- |

Part 1: Preliminary Electrical Safety Checks

Before carrying out any fault-finding or repair work, you must complete a series of safety tests to confirm that the appliance is safe to work on.

Safety Requirements:

- Always isolate the appliance before testing.

- Confirm isolation using approved safe isolation procedures.

- Wear appropriate PPE.

- Never carry out live testing in this exercise.

- Report any defects or hazards to your tutor immediately.

Task 1 – Earth Continuity Check

Procedure:

- Isolate the appliance (remove the plug from the socket outlet).

- Set your multimeter to the Ohms (Ω) ×1 scale.

- Test between any appliance earth point and the earth pin of the plug.

- Record the resistance reading.

Resistance reading =

Is this correct, if not what could be the issue?

Task 2 – Short Circuit Check

Procedure:

- Keep the appliance isolated.

- Ensure all switches are ON and thermostats are calling for heat.

- Set your meter to Ohms (Ω) ×1 scale.

- Test between L (live) and N (neutral) at the appliance terminal block.

- Record the meter reading.

Task 3 – Resistance to Earth Check

Procedure:

- Keep the appliance isolated.

- Set all switches ON and thermostats calling for heat.

- Set the meter to Ohms (Ω) ×100 scale.

- Test between L (live) and E (earth) at the appliance terminal block.

- Record the reading.

Reading =

Task 4 – Mains Voltage and Polarity Check (Tutor Demonstration Only)

Verify correct voltage and polarity before operation.

Procedure:

- This test must only be demonstrated by the tutor using live test procedures.

- Observe correct use of a voltage indicator or multimeter.

- Note safe testing practices and correct polarity results.

Note: These tests must always be completed in order and repeated after any electrical connections are disturbed or replaced.

Part 2: Practical Testing on Components

Set-Up: You will be provided with a range of electrical components (both operational and faulty).

Task:

Carry out the relevant tests from Part 1 on each component.

Record all readings and identify whether each component is safe or defective.

No live testing is to be performed – all components must be isolated and dead.

Part 3: Fault-Finding on a Working Appliance/System

Set-Up: Faults will be introduced into a working appliance or system.

Task:

Perform the required safety checks from Part 1.

Use the test methods to diagnose and locate the fault.

Repair or report the fault as appropriate.

Re-test after repair to confirm safe operation.

Part 4: Temporary Continuity Bonds Exercise

Learning Objective: To safely install temporary continuity bonds and confirm electrical continuity during pipework modifications.

Set-Up:

You will be given a pipework exercise linked to a previous plumbing activity.

The task involves cutting into an existing gas supply and fitting a tee and a short pipe section.

Task:

Fit temporary continuity bonds across the section to be cut.

Verify the effectiveness of the continuity bonds using a multimeter.

Remove the meter and carefully cut the pipe.

Install the tee and new pipework section.

Recommission the gas system following all safety procedures.

# Task 45: Recognition of controls

Your trainer will show you a selection of ten gas controls, you should name them and describe how they work:

| Control 1 |  |  |  | Control 2 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Control 3 |  |  |  | Control 4 |  |  |  |  |
| Control 5 |  |  |  | Control 6 |  |  |  |  |
| Control 7 |  |  |  | Control 8 |  |  |  |  |
| Control 9 |  |  |  | Control 10 |  |  |  |  |

Answer the following questions

On what appliance would control 1 be found?

Which two metals are bonded to form a bi-metallic strip?

Name the component activated by control 3.

Describe the use of control 4.

Identify the functions of a multifunctional control.

What is the correct name for a thermocouple?

Your trainer will now show you a controls rig. Identify the following controls from the rig allocated indicated by your trainer.

| Rig number |  |
| --- | --- |

| Control 1 |  |
| --- | --- |
| Description of operation: |  |
| Control 2 |  |
| Description of operation: |  |
| Control 3 |  |
| Description of operation: |  |
| Control 4 |  |
| Description of operation: |  |
| Control 5 |  |
| Description of operation: |  |

| Control 6 |  |
| --- | --- |
| Description of operation: |  |
| Control 7 |  |
| Description of operation: |  |
| Control 8 |  |
| Description of operation: |  |

Answer the following questions:

For the purposes of these questions, the Gas Safety (Installation and Use) Regulations will be abbreviated to ‘GSIUR’.

What is the purpose of a pressure regulator?

List the different types of pressure regulator.

Briefly describe the operation of a compensated constant pressure regulator.

| Learner signature: | Trainer signature: |
| --- | --- |

# Task 46: IGEM G/13 Procedures

You will now learn how to correctly carry out the process for IGEM/G/13 with different combinations of appliances. Your trainer will have set up a minimum of 5 situations where there are faults. You shou follow the correct IGEM G/13 procedures. You can refer to IGEM G/13 whilst carrying out this task.

Using the installation given to you by your trainer you should follow the steps below to check all appliances and pipework.

- Preparation and Safety

  - Review the current edition of IGEM/G/13.

  - Ensure your test area is safe, and equipment is operational.

  - Check tools and instruments are calibrated and in good condition.

- Appliance Assessment

  - Examine the range of appliances given to you by your trainer (e.g. boiler, cooker, and fire).

  - Check installation, operation, and ventilation.

  - Take necessary measurements such as burner pressure, gas rate, and flue performance.

  - Identify any non-compliances or unsafe conditions in the table on the next page:

- Classify Each Situation

  - Using the IGEM/G/13 flowchart, determine the correct classification for each fault or unsafe condition:

    - Immediately Dangerous (ID)

    - At Risk (AR)

    - Safe

- Follow Correct Reporting and Handover Process

  - Demonstrate how to fill in the warning notices and documentation accurately.

  - Explain to the “customer” (role-play) what the issue is and what actions must be taken.

  - Ensure the system is left in a safe condition before finishing.

|  | Appliance name/Location | Safe/A.R/I.D | Fault and Corrective measure |
| --- | --- | --- | --- |
| Fault 1 |  |  |  |
| Fault 2 |  |  |  |
| Fault 3 |  |  |  |
| Fault 4 |  |  |  |
| Fault 5 |  |  |  |

# Task 47: Gas safety (Installation and Use) regulations

You may use a textbook for the following questions.

According to the Regulations, what is an ‘appropriate fitting’?

Which type of valve cannot be regarded as an emergency control?

What is meant by the term ‘gas’?

Describe installation pipework as referred to in the GSIUR.

What type of premises are covered by the GSIUR?

According to Regulation 3, what is the duty of the employer in respect of gas installations?

The guidance on Regulation 3 states that competence depends on which two aspects?

Regulation 5(2) (GSIUR) makes reference to two materials that are not suitable for gas fittings. What are they?

According to Regulation 6(7), what cannot be fitted in a cellar or basement?

To which Regulation does the following statement relate:

‘A person who allows gas to flow into any premises for the first time should ensure an appropriately sited emergency control is in place.’

Quote the appropriate Regulation to be observed when installing temporary continuity bonding before undertaking gas installation work on existing installations.

With regard to emergency notices, who has the responsibility for ensuring that an appropriate emergency notice is in place at the meter?

Where is main equipotential bonding required?

With respect to Regulation 19, what does ‘the appropriate standard’ describe?

According to the guidance given with Regulation 22, what should be completed before pipework or joints on a gas installation are painted?

Regulation 26 requires that used gas appliances be inspected before being installed. Why is this necessary?

If an appliance cannot be commissioned immediately after being installed and connected to the gas supply, what action must an installer take?

Where an installer performs work on an appliance, what should immediately thereafter be examined?

Complete the following Regulation:

‘No person shall install a gas appliance except in such a manner that it is readily accessible for........’

Which type of appliance can be installed in a bathroom or shower room?

Under Regulation 36, give at least one definition of a ‘relevant gas fitting’:

According to the Regulations, copy of any relevant record must be given to a tenant by the landlord within what time frame?

What is the primary duty on a gas supplier in the event of an emergency?

Where can the name and means of contacting the gas supplier in an emergency be found?

Which government body may issue exemptions to liability under the GSIUR?

| Learner signature: | Trainer signature: |
| --- | --- |

GIUSP Scenarios

You will now be given 10 scenarios, it is up to you to identify the fault, state whether it is Safe, A.R or I.D. You then need to find and record which regulation this contravenes.

  - You arrive at a semi-detached property to carry out a landlord gas safety check. As you walk around the exterior, you notice the boiler flue terminal is positioned directly beneath an openable bedroom window, less than 300mm away. The flue gases could easily re-enter the property if the window is open.

  - You’re inspecting a combi boiler located in a hallway cupboard. Upon opening the door, you find the space crammed with coats, cardboard boxes, and cleaning products. The boiler’s ventilation grille is completely blocked.

  - You enter a lounge to inspect a decorative open-flame gas fire. Above the fire, you notice black staining on the wall and a faint smell of combustion products. You perform a flue flow and spillage test, which fails.

  - You’re inspecting a kitchen in a rented flat. The freestanding gas cooker is installed correctly in terms of pipework and ventilation, but when you gently pull the oven door, the appliance tips forward. You check behind and confirm there’s no stability bracket or chain fitted.

  - You’re called to inspect a property where the gas meter is located in a hallway cupboard. Upon opening it, you find the cupboard is sealed with no ventilation grilles. You test for gas and find no immediate leak.

  - You arrive at a property where the tenant reports a smell of gas in the kitchen. You attempt to access the Emergency Control Valve (ECV), but it’s boxed in behind a fixed kitchen unit with no access panel.

  - You’re inspecting a newly installed gas fire in a living room. The homeowner says it was fitted two weeks ago but no one tested it. You find no commissioning paperwork, no flue flow test results, and no tightness test record.

  - You’re inspecting a property where the homeowner has run copper pipework from the kitchen to an outdoor BBQ area. The pipework is clipped loosely, has no sleeve where it passes through the wall, and terminates with a (Water) service valve.

  - You’re inspecting a newly renovated kitchen with a modern gas hob. The room has no openable windows and no mechanical ventilation. You ask about the installation and find no record of ventilation assessment.

  - You arrive at a rental property to carry out a landlord gas safety check. The tenant mentions the gas fire has never been serviced since they moved in five years ago. You inspect the appliance and find dust buildup, poor flame picture, and signs of wear.

|  | GIUSP Classification | Regulation Contravened |
| --- | --- | --- |
| 1. |  |  |
| 2. |  |  |
| 3. |  |  |
| 4. |  |  |
| 5. |  |  |
| 6. |  |  |
| 7. |  |  |
| 8. |  |  |
| 9. |  |  |
| 10. |  |  |

# Task 48: Written report of maintenance activity

Your trainer will give you three gas faults on one or more appliances you must provide a detailed account of the fault diagnosis procedure, possible solutions and how you are going to rectify the problem.

Your report MUST be clear and detailed.

You MUST provide reasoning to support the methods selected to rectify the fault.

Reference MUST be made to informing the customer, safe isolation, equipment and materials required and to the use of manufacturer instructions during fault diagnosis.

Fault Report 1

Details of the fault:

Description of fault diagnosis:

Actions taken to rectify the fault:

Fault Report 2

Details of the fault:

Description of fault diagnosis:

Actions taken to rectify the fault:

Fault Report 3

Details of the fault:

Description of fault diagnosis:

Actions taken to rectify the fault:

# General Notes:

Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.

‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.

WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.

WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.

# Acknowledgements

Images used within these resources have been created using artificial intelligence (AI) and is intended to provide a visual representation only.

p.8 PashaIgnatov / iStock / Getty Images; p.8 Apriori1 / iStock / Getty Images; p.12 Wavebrak Media / Freepik.com; p.12 Image by Macrovector / Freepik.com; p. 12 EyeEm / Freepik.com; p.12 Image by Freepik.com; p.12 Image by mrsiraphol / Freepik.com; p.12 Mihalec / Freepik.com; p.13 indigolotos / iStock / Getty Images; p.13 nipastock / iStock / Getty Images; p.13 harsh2030fp / Freepik.com; p. 13 Mido.PXl / Freepik.com; p.13 FabrikaCr / iStock / Getty Images; p.14 image by brgfx / Freepik.com; p.14 cynoclub / Freepik.com; p.14 Kamiphoto / Freepik.com; p.14 Pineapple_Studio / Freepik.com; p.14 Francesco Marzovillo / iStock / Getty Images; p. 14 nonillion / iStock / Getty Images; p.15 vitaliiborkovskyi / Freepik.com; p.15 karayuschij / iStock / Getty Images; p.15 Nigel Stripe / iStock / Getty Images; p.15 kharlamov543211 / Freepik.com; p.15 LaymanZoom / iStock / Getty Images; p.16 rookman / iStock / Getty Images; p.18 MikeyGen73 / iStock / Getty Images; p. 18 EyeEm / Freepik.com; p.50 popovaphoto / iStock / Getty Images; p.50 user16172657 / Freepik.com; p.50 user15327819 / Freepik.com;