## Slide 1
Occupational Specialism: Gas Engineering
K1.19 Different techniques for forming and bending pipework
PowerPoint 1.19: Techniques for bending gas pipework safely and accurately

## Slide 2: Starter
Charlie is installing a new copper gas pipe around a doorway.
Should he use elbows or bend the pipe?
What factors should influence his choice?
Notes: Introduce the concept of flow rate, pressure loss, and pipe sizing.

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify tools used for bending gas pipework.
Describe correct procedures for forming bends.
Compare when to use a bending machine or spring.
Apply safe and accurate bending practices during installation.

## Slide 4: Why form pipe bends?
Reduces the number of fittings (e.g. elbows)
Minimises risk of leaks at joints
Improves gas flow by reducing turbulence
Tidier installation in visible areas (e.g. exposed copper pipes)
Can be more cost-effective over time

## Slide 5: Method 1: Bending machine
Use: Creates clean, uniform bends in copper and light steel pipe
Types:
  Hand-held mini benders (≤ 15 mm)
  Stand or hydraulic benders (15–28 mm+)
Steps:
  Mark centreline of bend on pipe
  Insert into correct former and guide
  Pull handles evenly until required angle e.g. 90°

## Slide 6: Method 1: Bending machine
Advantages:
  No kinks or flattening
  Precise radius
Limitations:
  Requires space to operate
  Not suitable for tight locations

## Slide 7: Method 2: Bending spring
Use: For small diameter pipe (typically 15 mm) in tight spaces
Type: Internal or external spring
Steps:
  Insert spring into or around pipe
  Slowly bend by hand around knee or a solid form
  Carefully remove spring after forming

## Slide 8: Method 2: Bending spring
Advantages:
  Portable and inexpensive
  Good for on-site adjustments
Limitations:
  Less precise than machine
  High risk of kinking if done too quickly or without support

## Slide 9: Comparison table
Feature | Bending machine | Bending spring
Accuracy | High | Medium
Pipe sizes | 15 mm – 28 mm+ | Typically ≤ 15 mm
Portability | Low (stand type) | High
Skill level | Moderate | Requires practice
Risk of kinking | Very low | Medium to high
Use case | Bench/workshop install | Confined space repair

## Slide 10: Safety and best practice
Inspect pipe and tool before use (no dents, wear, cracks).
Use the correct former size for the bending machine.
Never heat a gas pipe to bend it.
Always remove internal springs carefully.
Pipes must be re-rounded if ovalised before jointing.
Bends must not reduce the internal diameter or cause restriction.

## Slide 11: Summary
You should now be able to:
Identify tools used for bending gas pipework.
Describe correct procedures for forming bends.
Compare when to use a bending machine or spring.
Apply safe and accurate bending practices during installation.

## Slide 12
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.