## Slide 1
Occupational Specialism: Plumbing & Heating Engineering
K1.24 Factors to inspect during commissioning, and how expected standards are defined
PowerPoint 1.24a: Commissioning – tests, tools, and compliance checks

## Slide 2: Starter
Mark installs a new combi boiler and skips the standing pressure and gas rate checks. Two weeks later, the customer reports poor hot water pressure and yellow flames.
What has gone wrong?
What should Mark have done during commissioning?
Why are multiple tests needed, not just one?

## Slide 3: Objectives
By the end of this session, you should be able to:
List the key commissioning tests required after appliance installation.
Describe the purpose of each test (e.g. gas rate, combustion analysis).
Identify the tools used to perform these commissioning checks.
Explain how to confirm readings against expected values in the manufacturer’s instructions.

## Slide 4: What is commissioning?
Commissioning is the formal process of verifying that a newly installed or modified gas appliance or system meets all safety, performance and regulatory requirements before being put into service.
It represents the critical final stage of installation work and must be completed before handing over to the customer.

## Slide 5: What is commissioning?
The commissioning process ensures the appliance:
operates safely
meets efficiency standards
complies with Gas Safety regulations
follows manufacturer guidelines
provides baseline data for maintenance
fulfils contractual requirements.

## Slide 6: What is commissioning?
Proper commissioning includes both thorough visual inspection and comprehensive functional testing.
The visual inspection confirms proper installation according to regulations and standards, while functional testing verifies operational parameters meet requirements.
Commissioning must be performed by a Gas Safe registered engineer with the appropriate qualifications for the specific appliance type.
The results must be recorded on a commissioning certificate that becomes part of the appliance documentation.

## Slide 7: Key commissioning checks: overview
Test / Factor | Purpose | Expected range | Consequences if failed
Standing pressure | Confirms adequate inlet pressure before ignition | 19-23 mbar (NG) | Appliance starvation, incomplete combustion
Operating pressure | Verifies pressure stability during operation | ≤2 mbar drop from standing | Cycling, flame failure, inefficient operation
Burner pressure | Checks appliance gas control valve function | As per manufacturer's instructions | Poor combustion, efficiency loss
Gas rate (m³/h) | Confirms input matches rating plate | ±5% of rated input | Overheating, underperformance, efficiency loss
Combustion analysis | Assesses CO/CO₂ ratio, flue integrity | CO/CO₂ ratio <0.004 | CO production, potential poisoning risk
Flow rate (DHW) | Confirms water performance | As per rating plate (l/min) | Customer dissatisfaction, callbacks
Temperature rise | Indicates DHW heat transfer effectiveness | Typically 35–45°C rise | Scalding risk or inadequate heating

## Slide 8: Required tools and equipment
Digital manometer
Essential for measuring standing and operating pressures. Modern digital versions provide more precise readings than traditional U-gauge manometers. Must be calibrated annually and zeroed before each use. Typically measures in mbar or inches water gauge (inwg).

## Slide 9: Required tools and equipment
Gas meter and stopwatch
Used together for measuring gas rate via the test dial. Requires precise timing of gas consumption over a measured period. Electronic stopwatches provide greater accuracy than manual timing. Different meter types (U6, E6, etc.) have different test dial volumes.

## Slide 10: Required tools and equipment
Combustion analyser
Sophisticated electronic device that measures CO, CO₂, O₂ levels and flue temperature. Must be calibrated every 6 months and fitted with appropriate filters. Essential for verifying safe combustion and detecting potential CO risks. Modern versions include printout capabilities.

## Slide 11: Required tools and equipment
Thermometer and flow cup
Used to measure temperature rise and flow rate (l/min) for DHW systems. Digital thermometers provide faster, more accurate readings than traditional mercury thermometers. Flow cups typically measure in litres and feature graduated markings for precise measurement.

## Slide 12: Standing pressure test
Purpose
A standing pressure test is to ensure that a regulator has “locked up” correctly and does not therefore allow the pressure in the system to reach pressures the system is not designed for.

## Slide 13: Standing pressure test
Expected values
Natural Gas (NG): 19-23 mbar (optimal: 21 mbar)
Liquefied Petroleum Gas (LPG): 37 mbar for propane, 28-30 mbar for butane
Method
Connect manometer to appliance test nipple.
Zero the manometer before taking readings.
Open gas supply but ensure the appliance is OFF.
Record the standing pressure.
Verify against the expected range.

## Slide 14: Standing pressure test
Common issues
Low pressure (<19 mbar NG): Indicates undersized pipework, restrictions, or supply issues.
High pressure (>23 mbar NG): Rare but may indicate regulator issues.
Fluctuating pressure: May indicate unstable supply or governor problems.
If the standing pressure is outside acceptable parameters, do not proceed with commissioning until the issue is resolved. This may require contacting the gas transporter for supply issues.

## Slide 15: Operating pressure test
Purpose
The operating pressure test verifies that adequate gas pressure is maintained when the appliance is running. It confirms that the gas supply infrastructure can meet the appliance's demands during operation.
Expected values
Pressure drop should not exceed 2 mbar from standing pressure.
Minimum operating pressure for NG: 17 mbar.
Pressure should remain stable during operation.

## Slide 16: Operating pressure test
Method
Leave manometer connected from standing pressure test.
Turn appliance on at maximum rate.
Allow system to stabilise (2–3 minutes).
Record operating pressure.
Calculate the pressure drop (standing – operating).

## Slide 17: Operating pressure test
Interpretation
An excessive pressure drop between standing and operating pressures indicates inadequate gas supply, typically caused by:
Undersized pipework relative to appliance demand.
Partially blocked gas filter or restrictor.
Excessive number of fittings causing pressure loss.
Multiple appliances competing for gas supply.
Inadequate gas meter capacity for total load.

## Slide 18: Burner pressure test
Purpose
The burner pressure test verifies that the appliance's internal gas control valve is delivering the correct pressure to the burner. This ensures the appliance receives its designed gas input for proper combustion.
Expected values
Varies by appliance model and type. Must be checked against the manufacturer's instructions. May have different values for maximum and minimum rates. Modern condensing boilers often use gas/air ratio valves instead of fixed pressure settings.

## Slide 19: Burner pressure test
Method
Connect manometer to burner pressure test point.
Zero the manometer.
Operate appliance at maximum rate.
Allow the appliance to reach normal working temperature (typically 10 minutes).
Record burner pressure.
If required, check at minimum rate also.

## Slide 20: Burner pressure test
Important considerations
Modern high-efficiency appliances often use different control methods:
Pre-mix burners may not have traditional burner pressure test points.
Gas/air ratio valves modulate based on air flow, not fixed pressure.
Some appliances use electronic gas valve control rather than mechanical pressure regulation.
Always refer to the manufacturer's specific commissioning instructions.
Never adjust gas valve settings unless specifically instructed by manufacturer documentation.

## Slide 21: Gas rate measurement
Purpose and principles
Gas rate testing confirms the actual gas consumption matches the appliance's rated input.
This ensures the appliance receives the correct amount of fuel for safe and efficient operation.
An incorrect gas rate can lead to overheating, incomplete combustion, or poor performance.

## Slide 22: Gas rate measurement – imperial
Equipment required
You'll need access to the gas meter, a stopwatch (preferably digital), and the manufacturer's instructions showing the rated input.
The calculation also requires knowledge of the meter's test dial volume (typically 2ft³ or 1ft³) and the gas calorific value (CV).

## Slide 23: Gas rate measurement – imperial
Steps to calculate gas rate with an imperial meter:
Ensure the appliance is running at its maximum setting. This is crucial for an accurate gas rate calculation.
Identify the test dial on the meter. It's a dial that completes one full revolution for a specific volume of gas (e.g. 1 cubic foot).
Start the stopwatch and time one full revolution of the test dial. Stop the stopwatch when the dial completes a full cycle.
Record the time in seconds: it took for the dial to complete one revolution.

## Slide 24: Gas rate measurement – imperial
Steps to calculate gas rate with an imperial meter:
Apply the formula:
Gas Rate (ft³/hr) = (3600 * Number of ft³ per revolution) / Time in seconds.
Example: If it takes 45 seconds for one cubic foot of gas to pass, the gas rate would be (3600 * 1) / 45 = 80 ft³/hr.
Convert to other units (optional): If you need the gas rate in other units, such as m³/hr or kW, you'll need to apply appropriate conversion factors.

## Slide 25: Gas rate measurement – imperial
Important notes:
The number of cubic feet per revolution varies depending on the meter type (e.g. U6, U16).
Some meters may have a test dial that represents 0.1 ft³ or other fractions of a cubic foot.
Ensure the test dial completes a full revolution for accuracy.
The gas rate should be within the manufacturer's specified limits for the appliance.
Always consult with a qualified Gas Safe registered engineer if you have any safety concerns or if the gas rate is outside the acceptable range.

## Slide 26: Gas rate measurement – metric
To determine the gas rate of an appliance with a metric meter, you need to measure the gas consumption over a specific time period and then calculate the rate in cubic meters per hour (m³/hr).
This involves noting the meter reading before and after running the appliance for a set duration, typically two minutes.

## Slide 27: Gas rate measurement – metric
Here's a breakdown of the process:
1. Ensure all other gas appliances are off:
This ensures accurate measurement of the appliance being tested.
2. Note the initial meter reading:
Record the reading from your metric gas meter before you turn on the appliance.
3. Run the appliance:
Turn on the appliance you want to test, ensuring it's operating at its maximum heat input (full power).

## Slide 28: Gas rate measurement – metric
4. Run the appliance for a specific time:
Operate the appliance for a set duration, typically two minutes.
5. Note the final meter reading:
After the set time, record the meter reading again.
6. Calculate the gas consumption:
Subtract the initial reading from the final reading to determine the volume of gas used (in cubic meters).

## Slide 29: Gas rate measurement – metric
7. Calculate the gas rate:
Use the following formula:
Gas rate (m³/hr) = (Gas used in m³ / Test time in seconds) * 3600.
8. Example:
If you used 0.053 m³ in 120 seconds, the calculation would be:
(0.053 / 120) * 3600 = 1.59 m³/hr.

## Slide 30: Gas rate measurement – heat input
Calculate heat input:
You can further calculate the heat input of the appliance using the gas rate and the calorific value of the gas (usually found on your gas bill).
Metric: Heat input (kW) = Gas rate (m³/hr) * Calorific value (MJ/m³) / 3.6. For example, using a calorific value of 38.76 MJ/m³ for natural gas, the heat input would be 1.59 * 38.76 / 3.6 = 17.11 kW.
Gross and net heat input:
You may also see references to gross and net heat input, which account for the heat content of the gas. The net heat input is typically lower than the gross heat input due to a conversion factor (e.g. dividing by 1.1).

## Slide 31: Combustion analysis
Purpose
Combustion analysis is one of the most critical safety tests performed during commissioning. It measures the products of combustion to ensure the appliance is burning gas safely and efficiently. This test directly identifies potential carbon monoxide hazards.

## Slide 32: Combustion analysis
Key measurements
Carbon Monoxide (CO) in parts per million (ppm).
Carbon Dioxide (CO₂) as a percentage (%).
Oxygen (O₂) as a percentage (%).
CO/CO₂ ratio – critical safety parameter.
Flue gas temperature.

## Slide 33: Combustion analysis
Expected values (High-Efficiency Condensing Boilers)
CO: Typically <10 ppm (never >350 ppm).
CO₂: 8.5-9.5% for NG (varies by manufacturer).
CO/CO₂ ratio: Must be <0.004 (critical safety limit).
Flue temperature: 45-75°C for condensing operation.

## Slide 34: Combustion analysis
Method
Ensure analyser is calibrated and in good working order.
Insert probe into appropriate flue test point.
Run appliance at maximum rate for 5+ minutes.
Allow readings to stabilise before recording.
Repeat at minimum rate if required by manufacturer.
Calculate CO/CO₂ ratio if not displayed automatically.

## Slide 35: Combustion analysis
Warning signs
Rising CO levels during operation.
CO/CO₂ ratio approaching 0.004.
CO₂ outside manufacturer's specification.
Abnormally high or low flue temperature.
If combustion analysis reveals unsafe readings, the appliance must not be left operational. Common causes include blocked heat exchangers, incorrect gas pressure, improper air/gas ratio, or flue restrictions. All adjustments must follow manufacturer guidelines precisely.

## Slide 36: DHW flow rate and temperature testing
Purpose
For combination boilers and instantaneous water heaters, testing the domestic hot water (DHW) flow rate and temperature rise is essential to verify performance meets both manufacturer specifications and user requirements.
Flow rate measurement
Measured in litres per minute (l/min).
Should match rated output on appliance data plate.
Typically 10–15 l/min for standard combi boilers.
Affected by incoming water pressure and temperature.
.

## Slide 37: DHW flow rate and temperature testing
Method
Use calibrated flow cup with measurement markings.
Open hot water tap to maximum flow.
Collect water for precisely 6 seconds.
Multiply volume by 10 to calculate l/min.
Compare to manufacturer's specification.

## Slide 38: DHW flow rate and temperature testing
Temperature rise measurement
Measured as difference between inlet and outlet temperatures.
Typically 35-45°C for combi boilers at rated flow.
Directly related to appliance power and flow rate.

## Slide 39: DHW flow rate and temperature testing
Method
Measure cold water inlet temperature.
Run hot water at rated flow for 2 minutes to stabilise.
Measure hot water outlet temperature.
Calculate temperature rise (outlet – inlet).
Verify against manufacturer's specification.

## Slide 40: DHW flow rate and temperature testing
Important relationship
For every 1kW of heat input, expect approximately 3.1 l/min flow rate with a 30°C temperature rise. Reducing the flow increases the temperature rise and vice versa.
Inadequate flow rates may indicate restrictions in the water circuit, heat exchanger scaling, or insufficient water supply pressure. Temperature issues may indicate incorrect gas input, faulty thermistors, or limescale buildup affecting heat transfer efficiency.

## Slide 41: Manufacturer's Instructions (MI)
Legal status
Manufacturer's Instructions have legal standing under the Gas Safety (Installation and Use) Regulations. Following MI is not optional – it is a legal requirement for Gas Safe registered engineers.
Critical parameters
MI specify acceptable ranges for all commissioning tests including pressures, gas rates, combustion values, and temperature settings. These values are specific to each appliance model.

## Slide 42: Manufacturer's Instructions (MI)
Stabilisation period
MI will specify required stabilisation periods before taking readings (typically 10–15 minutes). This ensures the appliance reaches steady-state operation for accurate measurements.
Adjustment limitations
MI clearly states which parameters may be adjusted by the installer and which require manufacturer intervention. Never adjust gas valves or air ratios unless explicitly authorised by MI.

## Slide 43: Manufacturer's Instructions (MI)
Finding the correct MI
Always use the MI specific to the exact model being commissioned.
Check manufacturer websites for the latest version.
Pay attention to revision dates and superseded documentation.
Some manufacturers now provide MI via mobile applications.
Keep physical or digital copies for reference and evidence.

## Slide 44: Benchmark Commissioning Checklist
The Benchmark Commissioning Checklist is a standardised document used across the UK heating industry to record that an installation has been commissioned correctly.
It forms part of the appliance warranty documentation and provides evidence of regulatory compliance.

## Slide 45: Benchmark Commissioning Checklist
Key sections
Installer and customer details.
Appliance information (make, model, serial number).
Gas type and pressure readings.
Combustion analysis results.
System flushing and water treatment confirmation.
Flow rates and temperature settings.
Safety device checks.
Customer handover confirmation.

## Slide 46: Benchmark Commissioning Checklist
Best practices
Complete all sections accurately and legibly.
Record actual measured values, not just ticks.
Leave the completed checklist with the appliance.
Provide a copy to the customer.
Retain a copy for your own records (minimum 6 years).
Some manufacturers now offer digital Benchmark apps.

## Slide 47: Troubleshooting commissioning issues
Low standing pressure
Symptoms: Standing pressure below 19 mbar (NG).
Possible causes:
Supply network issues.

## Slide 48: Troubleshooting commissioning issues
Low standing pressure solutions:
Check and fully open ECV.
Verify pipework sizing calculations.
Contact gas transporter for supply issues.

## Slide 49: Troubleshooting commissioning issues
Excessive pressure drop
Symptoms: >2 mbar drop between standing and operating pressure.
Possible causes:
Undersized pipework for appliance rating.
Restrictions in gas line (partially blocked filter).
Too many bends or fittings causing restrictions.

## Slide 50: Troubleshooting commissioning issues
Excessive pressure drop solutions:
Increase pipe diameter.
Clean or replace gas filter.
Reconfigure pipework to reduce restrictions.

## Slide 51: Troubleshooting commissioning issues
Combustion analysis failures
Symptoms: High CO, incorrect CO₂, poor CO/CO₂ ratio
Possible causes:
Incorrect gas/air ratio.
Heat exchanger blockage.
Flue restriction or incorrect installation.
Burner fouling.

## Slide 52: Troubleshooting commissioning issues
Combustion analysis failures solutions:
Check/adjust gas/air ratio per MI.
Clean heat exchanger/burner.
Verify flue installation meets requirements.

## Slide 53: Troubleshooting commissioning issues
Incorrect gas rate
Symptoms: Measured gas rate does not match rating.
Possible causes:
Incorrect gas pressure.
Gas valve misadjustment.
Incorrect injector size.
Gas meter accuracy issues.

## Slide 54: Troubleshooting commissioning issues
Incorrect gas rate solutions:
Verify and adjust pressures per MI.
Check injector size is correct for gas type.
Verify gas meter accuracy.

## Slide 55: Troubleshooting commissioning issues
When troubleshooting commissioning issues, always follow a systematic approach.
Start with the simplest checks first and work methodically through potential causes.
Document all findings and actions taken.
If you cannot resolve an issue safely, seek manufacturer support or specialist advice rather than leaving an appliance in an unsafe condition.

## Slide 56: Regulatory framework
Gas Safety (Installation and Use) Regulations 1998
The primary legislation governing gas work in the UK. Regulation 26(9) specifically requires that safety checks are to be carried out when any “work” is carried out on a gas appliance.

## Slide 57: Regulatory framework
Where a person performs work on a gas appliance he shall immediately thereafter examine—
(a)the effectiveness of any flue;
(b)the supply of combustion air;
(c)[subject to sub-paragraph (ca),] its operating pressure or heat input or, where necessary, both;
(ca)if it is not reasonably practicable to examine its operating pressure or heat input (or, where necessary, both), its combustion performance;]
(d)its operation so as to ensure its safe functioning.

## Slide 58: Regulatory framework
British Standards
Key standards relevant to commissioning include:
BS 6891: Installation of low-pressure gas pipework.
BS 5440-1: Flues for gas appliances.
BS 5440-2: Air supply for gas appliances.
BS 6798: Installation of gas-fired boilers.

## Slide 59: Regulatory framework
Industry standards
Additional guidance documents include:
IGEM/UP/1B: Tightness testing and purging.
IGEM/UP/10: Installation of flued gas appliances.
TB 143: CO and combustion ratio checks.
Manufacturer's Instructions (having legal status).

## Slide 60: Regulatory framework
Documentation requirements
Legal requirements for record keeping:
Benchmark commissioning checklist completion.
Gas safety record for landlord installations.
Building regulations notification (where applicable).
Records must be kept for minimum of 6 years.

## Slide 61: Summary
You should now be able to:
List the key commissioning tests required after appliance installation.
Describe the purpose of each test (e.g. gas rate, combustion analysis).
Identify the tools used to perform these commissioning checks.
Explain how to confirm readings against expected values in the manufacturer’s instructions.

## Slide 62
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.