## Slide 1
Occupational Specialism: Gas Engineering
K1.24 Factors to inspect during commissioning, and how expected standards are defined
PowerPoint 1.24b: Interpreting results and taking action during commissioning

## Slide 2: Starter
Charlie performs all commissioning tests on a new boiler. The combustion analysis shows a CO/CO₂ ratio outside of MI limits. The flame picture looks fine, so he leaves the job.
What is wrong with this decision?
Is a correct flame picture enough evidence of safety?
What should Charlie have done?

## Slide 3: Objectives
By the end of this session, you should be able to:
Interpret commissioning results and compare them against MI standards.
Assess appliance and system condition during visual inspection.
Identify when results indicate unsafe operation.
Describe the appropriate actions if an appliance/system does not meet expected standards.

## Slide 4: The importance of proper commissioning
Commissioning is a critical safety procedure that ensures gas appliances operate efficiently and safely. Proper commissioning:
Confirms the installation meets regulatory requirements.
Verifies appliance performance matches manufacturer specifications.
Establishes baseline readings for future servicing.
Prevents potential hazards including carbon monoxide poisoning.
Fulfils legal obligations under Gas Safety Regulations.

## Slide 5: Standing and operating pressure
Standing pressure
Measured with appliance off
Indicates adequacy of gas supply
Natural Gas: 20-23 mbar typical
LPG: 37 mbar (propane), 28-30 mbar (butane)
If below 19 mbar (NG), investigate supply issues before proceeding.

## Slide 6: Standing and operating pressure
Operating pressure
The operating pressure for gas appliances is defined as the pressure measured at the appliance inlet when the appliance is running under normal conditions.
A maximum pressure drop of 1 mbar is generally acceptable between the meter outlet and the appliance inlet.
Standard Operating Pressure: Natural gas (G20): 20 mbar ± 2 mbar at the appliance inlet.

## Slide 7: Gas rate and burner pressure
Gas rate measurement
Use U6/G4 meter for timing.
Convert kW to m³/h using formula.
Should be within ±5% of MI value.
High rate may indicate over-gassing.
Low rate suggests restrictions.
Formula: Gas rate (m³/h) = Input rating (kW) ÷ Calorific value (MJ/m³) × 3.6

## Slide 8: Gas rate and burner pressure
Burner pressure
Check against data plate values.
Usually 10-13 mbar for NG appliances.
Adjust only if permitted by MI.
Low pressure causes incomplete combustion.
High pressure wastes gas and can damage components.

## Slide 9: Combustion analysis
Key measurements
CO/CO₂ ratio (most critical safety parameter).
CO (ppm) – Carbon Monoxide level.
CO₂ (%) – Carbon Dioxide percentage.
O₂ (%) – Oxygen percentage.
A CO/CO₂ ratio >0.004 indicates incomplete combustion and represents a significant safety risk that must be addressed immediately.
Modern analysers calculate the CO/CO₂ ratio automatically, but you should understand how to interpret the individual readings as well.

## Slide 10: Visual inspection during commissioning
Burner condition
No corrosion or sooting
Uniform flame pattern
No flame lift or spillage
Clean jets and venturi

## Slide 11: Visual inspection during commissioning
Appliance casing
Securely fitted
Properly sealed
Undamaged panels
Correct clearances

## Slide 12: Visual inspection during commissioning
Ventilation
Present as specified
Unobstructed openings
Correct sizes
Free airflow

## Slide 13: Visual inspection during commissioning
Flue system
Properly connected
Correctly sealed
Terminal compliance
Test point accessible
Document all visual inspection findings on the commissioning sheet with photographic evidence where appropriate.

## Slide 14: Flame assessment
Correct flame characteristics
Blue flame with slight inner cone.
Stable with no lift or floating.
No yellow tipping or luminosity.
Quiet operation without rumbling.
Even distribution across the burner.
Important: Visual assessment alone is NOT sufficient for safety verification. Instrument testing is mandatory.

## Slide 15: Common flame faults
Yellow tipping
Indicates incomplete combustion due to insufficient primary air or blocked injectors. High risk of CO production.
Flame lift
Occurs when gas/air mixture velocity exceeds flame speed. May indicate excessive pressure or incorrect air/gas ratio.
Sooting
Black carbon deposits indicate severe incomplete combustion. Requires immediate attention and likely component cleaning.

## Slide 16: Documentation requirements
Required documentation
Manufacturer's Instructions (MI).
Appliance data plate details.
Commissioning log sheet.
Benchmark certificate (where applicable).
Building Regulations notification.
Gas Safety Record (landlord installations).

## Slide 17: Manufacturer's Instructions (MI)
MI defines:
Specific test values for the appliance.
Required flow rates and temperatures.
Permitted adjustments and procedures.
Pre-commissioning checks.
Sequence of operations.
Maintenance requirements.
Never guess values or procedures. Always refer to the specific MI for the appliance being commissioned.

## Slide 18: What if something fails?
Stop the job
If test results are outside MI tolerances, the appliance must not be used until rectified. Inform the customer immediately.
Check for user-side errors
Investigate potential simple causes like blocked filters, closed valves, or incorrect settings.

## Slide 19: What if something fails?
Re-test after checking connections
Verify all testing equipment is correctly connected and functioning properly, then repeat the tests.
Take appropriate action if unsafe
Classify under IGEM/G/11, isolate the appliance, apply warning label, inform the responsible person, and complete an Unsafe Situation Report.

## Slide 20: Understanding IGEM/G/11 classifications
AR – At Risk
A situation where an installation is dangerous, but not immediately hazardous. The gas emergency service provider should be notified if required.
Example: Insufficient permanent ventilation but no immediate danger.

## Slide 21: Understanding IGEM/G/11 classifications
ID – Immediately Dangerous
A situation that presents an immediate danger to life or property. The appliance must be disconnected and sealed immediately.
Example: CO/CO₂ ratio above safe limits or gas leak detected.

## Slide 22: Required actions for unsafe situations
Isolation procedure
Turn off the appliance.
Close and label the gas isolation valve.
Apply appropriate warning label.
Attempt to remove key components if necessary.
Disconnect and cap if ID classification.

## Slide 23: Required actions for unsafe situations
Documentation
Complete an Unsafe Situation Report.
Document all test readings as evidence.
Obtain signature from the responsible person.
Provide a copy to the customer and keep one for the records.
Report to Gas Safe Register if required.

## Slide 24: Required actions for unsafe situations
Communication
Clearly explain the hazard to the customer.
Use non-technical language.
Explain legal implications of tampering.
Provide written confirmation.
Recommend remedial actions.

## Slide 25: Key non-compliances to spot
Issue | Action required
No flue test point | Cannot complete FGA test – fit test point or classify as unsafe.
Missing ECV label | Must apply new one before completing commissioning.
CO above safe rate | Investigate cause – adjust if permitted or cap off as ID.
Insufficient ventilation | Report and do not commission until rectified.
Flame lift or yellow flames | Recheck burner pressure/combustion and identify root cause.
Incorrect flue terminal location | Document non-compliance and refuse commissioning.
Appliance not to current standards | Assess risk level and classify accordingly.

## Slide 26: DHW flow rate testing
Testing procedure
Set appliance to DHW mode at maximum temperature.
Fully open hot water tap.
Measure flow rate using flow cup or container and stopwatch.
Calculate litres per minute.
Compare to MI specifications.
Formula: Flow rate (l/min) = Volume (litres) ÷ Time (seconds) × 60

## Slide 27: Case study: commissioning gone wrong
The incident
A new combi boiler installation passed visual inspection with perfect blue flames. Due to time constraints, the engineer skipped full FGA testing. Two weeks later, the residents suffered carbon monoxide poisoning.
The investigation
Subsequent testing revealed a CO/CO₂ ratio of 0.008—twice the safe limit. Debris had partially blocked the flue, restricting exhaust flow despite normal flame appearance.

## Slide 28: Case study: commissioning gone wrong
Legal consequences
Engineer prosecuted under the Gas Safety Regulations.
£5,000 fine plus legal costs.
Gas Safe registration suspended.
Civil claim from the affected family.
This real case demonstrates why visual inspection alone is never sufficient. Complete testing is not optional – it's a legal requirement.

## Slide 29: Best practice recommendations
Always verify – Double-check readings and calibrate instruments regularly. Never rely on a single measurement when safety is concerned.
Document everything – Comprehensive records protect both customers and engineers. Take photos of test points and readings as additional evidence.
Explain clearly – Ensure customers understand test results and any actions taken. Use simple language and provide written information.
Continuous learning – Stay updated with changing standards and manufacturer specifications. Attend regular training on new equipment.

## Slide 30: Gas rate measurement
Purpose and principles
Gas rate testing confirms the actual gas consumption matches the appliance's rated input.
This ensures the appliance receives the correct amount of fuel for safe and efficient operation.
An incorrect gas rate can lead to overheating, incomplete combustion, or poor performance.

## Slide 31: Summary
You should now be able to:
Interpret commissioning results and compare them against MI standards.
Assess appliance and system condition during visual inspection.
Identify when results indicate unsafe operation.
Describe the appropriate actions if an appliance/system does not meet expected standards.

## Slide 32
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.