## Slide 1
Occupational Specialism: Gas Engineering
K1.25 – Testing of installation
PowerPoint 1.25a: Tightness testing

## Slide 2: Starter
Simon replaces a gas hob in a domestic kitchen. After installation, he doesn’t carry out a tightness test, saying ‘it’s only a small job’.
Discussion questions:
Why is this risky?
What could happen if a joint is slightly loose or damaged?
What might the Gas Safe Register or IGEM/G/11 say about this approach?
Notes: Learners work in pairs or small groups to list at least 3 reasons why tightness testing is essential, especially after any installation or alteration.

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe the purpose and principles of tightness testing in gas systems
Identify the equipment required and its correct application
Explain how tightness tests are carried out on low-pressure installations
Evaluate test results to determine whether a system is safe or if further investigation is needed

## Slide 4: Importance of testing gas installations
Gas tightness testing is not merely a regulatory requirement—it's a fundamental safety measure that protects lives and property throughout the UK. This critical procedure provides:
Safety assurance
Provides essential verification that gas installations are leak-free before commissioning, preventing potentially catastrophic gas escapes.

## Slide 5: Importance of testing gas installations
Legal compliance
Fulfils requirements under the Gas Safety (Installation and Use) Regulations 1998, which mandate proper testing before gas is supplied.
Health protection
Prevents exposure to carbon monoxide and other harmful gases that could lead to serious illness or fatality.

## Slide 6: What is a gas tightness test?
Definition
A systematic pressure test aimed at detecting leaks in gas piping, fittings, and associated appliances prior to initiating gas flow through the system.
Methodology
Employs a calibrated U-gauge manometer to monitor pressure variations within a sealed gas system, verifying that the installation preserves the required pressure integrity.

## Slide 7: What is a gas tightness test?
Scope
Includes the whole gas system starting from the Emergency Control Valve up to every appliance isolation valve, guaranteeing a thorough safety check.

## Slide 8: When is tightness testing required?
Gas tightness testing is a mandatory requirement in specific circumstances to ensure the continued safety and integrity of gas installations:
After the installation of new gas pipework or appliances
Following any modifications to existing gas systems
Before purging and commissioning with fuel gas
After completing repairs to gas installations

## Slide 9: When is tightness testing required?
As part of routine maintenance procedures
When investigating suspected gas leaks
Following any incident that might compromise installation integrity

## Slide 10: When is tightness testing required?
New installation – Initial verification before first use
System modification – Testing after changes to existing pipework
Pre-commissioning – Final check before the system goes live
Post-repair – Verification after fixing identified issues

## Slide 11: Preparation: safety precautions
Ensure all appliances are off
Verify that all gas appliances are properly shut down and that all isolation valves are in the closed position to prevent gas flow during testing.
Eliminate ignition sources
Remove or disable any potential ignition sources in the testing area, including electrical equipment, open flames, and smoking materials.

## Slide 12: Preparation: safety precautions
Notify responsible persons
Inform the property owner or responsible person about the testing procedure, explaining the process and any potential disruptions to service.

## Slide 13: Step 1: Isolate and access the meter
Locate the gas meter and Emergency Control Valve (ECV)
Turn the ECV to the "OFF" position, completely stopping gas flow
Verify that gas flow has ceased by checking appliances
Identify the test nipple on the outlet side of the gas meter
Carefully unscrew the test nipple using the appropriate tool
Connect the U-gauge manometer to the test nipple, ensuring a secure connection
Verify the U-gauge is properly calibrated and reads zero

## Slide 14: Step 2: Let-by test
Pressurisation – Briefly crack open the ECV to introduce gas pressure between 7-10 millibars, then close it completely.
Observation – Monitor the U-gauge for exactly one minute, looking for any movement in the water column that indicates leakage.
Assessment – If no movement is observed, the ECV passes the let-by test. Any rise or fall requires further investigation.
The let-by test is crucial as it verifies that the Emergency Control Valve is functioning correctly and not allowing gas to pass when in the closed position. Any leakage at this point would compromise the subsequent tightness test and pose a safety risk.

## Slide 15: Step 3: Temperature stabilisation
Why temperature stabilisation matters
Temperature fluctuations can significantly affect pressure readings, potentially leading to false results. This stabilisation period ensures accurate measurements by:
Allowing the gas to reach thermal equilibrium within the pipework
Minimising the effect of thermal expansion or contraction on pressure readings
Providing a consistent baseline for the subsequent tightness test
Ensuring compliance with industry best practices and BS 6891 standards

## Slide 16: Step 3: Temperature stabilisation
Initial Pressurisation
Raise system pressure to exactly 20 millibars by carefully opening the ECV
Holding Period
Maintain pressure for 1 minute, adjusting as necessary to compensate for initial temperature effects
Readiness Check
Verify a stable 20 millibar reading before proceeding to the formal tightness test

## Slide 17: Step 4: Conduct tightness test
Set test pressure – Ensure the system pressure is precisely at 20 millibars after the stabilisation period has completed. This is your baseline measurement.
Begin test period – Start timing for exactly 2 minutes (longer for larger installations as per BS 6891). Record the exact starting pressure reading.
Monitor U-Gauge – Observe the U-gauge continuously throughout the test period, looking for any drop in pressure that indicates a leak in the system.

## Slide 18: Step 5: Interpreting results
4 mbar G4 Meter Limit – Maximum acceptable pressure drop for standard domestic meter during 2-minute test period
8 mbar E6 Meter Limit – Maximum acceptable pressure drop for larger domestic/small commercial meter during 2-minute test period
0 mbar Ideal Result – Optimum outcome indicating perfect system integrity with no detectable leakage

## Slide 19: Procedure for evaluating results
Test results should follow strict industry standards:
Record the pressure drop in millibars
Compare it to the allowable limit for the meter type, and note any gas odour
Exceeding limits or detecting odour means failure
Document results and extend testing if results are borderline

## Slide 20: Step 6: Final checks and recommissioning
Remove test equipment
Turn ECV to off position, carefully disconnect the U-gauge manometer, and properly reseal the test nipple to ensure gas-tight integrity.
Apply leak detection fluid
Spray approved LDF on all connections including the test nipple, meter joints, and visible pipework to verify absence of leaks.

## Slide 21: Step 6: Final checks and recommissioning
Restore gas supply
If all tests pass and no leaks are detected, carefully open the ECV to restore gas supply to the installation.
Verify appliance operation
Check that all appliances function correctly with restored gas supply, verifying normal operation and flame patterns.

## Slide 22: Post-test actions for failures
Leak tracing methodology
Divide the system into sections to isolate the leak location
Use electronic gas detectors to pinpoint precise leak sources
Apply leak detection fluid to all joints and connections
Inspect appliance connections and flexible hoses

## Slide 23: Post-test actions for failures
Immediate safety measures
Maintain ventilation throughout leak investigation
If a significant leak is detected, isolate the supply at ECV
Issue a warning notice for unsafe installations
Contact Gas Transporter for upstream leaks

## Slide 24: Post-test actions for failures
Repair and verification
Replace faulty components with approved parts
Properly seal all joints using appropriate methods
Conduct a full tightness test after all repairs
Document all repairs and subsequent test results

## Slide 25: Documentation and compliance
Required documentation
Proper record-keeping is essential for regulatory compliance and safety assurance:
Detailed test results, including pressure readings and drop measurements
Description of installation tested, including pipe materials and sizes

## Slide 26: Documentation and compliance
Required documentation
Details of any repairs or modifications made to achieve compliance
Signed declaration confirming installation meets BS 6891 standards
Gas Safe Register notification for notifiable work

## Slide 27: Documentation and compliance
Regulatory framework
UK gas installations are governed by strict regulatory requirements:
Gas Safety (Installation and Use) Regulations 1998
BS 6891:2015 Specification for installation of low-pressure gas pipework
Industry Standard Service Procedures for gas operatives
Gas Safe Register technical bulletins and guidance

## Slide 28: Documentation and compliance
Record retention
Documentation must be maintained for safety and legal purposes:
Copy provided to property owner/responsible person.
Records kept by gas engineer for a minimum of 6 years.
Documentation must be available for audit by the Gas Safe Register.
Records may be required as evidence in case of incidents.

## Slide 29: Fundamental safety foundation
Gas tightness testing represents the cornerstone of gas installation safety in the UK, providing the essential verification that systems are leak-free before commissioning. This critical procedure:
Prevents potentially catastrophic gas escapes and explosions.
Protects building occupants from carbon monoxide poisoning.
Ensures compliance with stringent UK safety regulations.
Provides documented evidence of installation integrity.
Establishes baseline performance for future reference.
By methodically applying the procedures outlined in this presentation, gas engineers fulfil their professional and legal obligations whilst safeguarding lives and property.

## Slide 30: Summary
You should now be able to:
Describe the purpose and principles of tightness testing in gas systems.
Identify the equipment required and its correct application.
Explain how tightness tests are carried out on low-pressure installations.
Evaluate test results to determine whether a system is safe or if further investigation is needed.

## Slide 31
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.