## Slide 1
Occupational Specialism: Gas Engineering
K1.26 Safe storage and supply of fuel source
PowerPoint 1.26a: Natural Gas

## Slide 2: Starter
Ash is working in a basement flat and finds the gas meter boxed in, with no visible emergency control valve (ECV). The pipe enters through a wall, and no labels are present.
What are the safety issues here?
What legal requirements apply to NG supply installations?
How should this meter and pipework be set out?

## Slide 3: Objectives
By the end of this session, you should be able to:
Describe how Natural Gas is stored and supplied to domestic and light commercial premises.
Identify the correct layout and equipment involved in NG installations (meters, ECVs, pipe entry).
Explain how to ensure safe access, ventilation, and compliance with regulations.
Evaluate risks and non-compliances in NG meter and supply arrangements.

## Slide 4: Gas supply system in the UK
Britain currently sources its gas from a variety of suppliers to ensure a steady supply for the country.
These sources include:
Production from the North and Irish Seas.
Pipelines connecting to continental Europe and Norway.
Liquefied Natural Gas (LNG) imported from global locations.
Typically, gas from the North and Irish Sea fields accounts for about 40% of the supply. However, as production from these fields decreases, the country is increasingly relying on imports for its gas needs.

## Slide 5: The four gas pipelines
The UK–Belgium interconnector (IUK): Extends from Bacton in Norfolk to Zeebrugge in Belgium, linking Britain to the mainland European gas network with a capacity of 25.5 billion cubic metres per year (BCM).
The UK–Netherlands pipeline: Runs between Balgzand and Bacton in Norfolk, offering an import capacity of 14.2 BCM annually.

## Slide 6: The four gas pipelines
The Vesterled pipeline link: Connects St Fergus in Scotland to multiple Norwegian gas fields, with a capacity of 14.2 BCM per year.
The Langeled pipeline: At 1,200 km, it is the longest subsea gas pipeline globally, stretching from Nyhamna in Norway to Easington in Yorkshire. It has a capacity of 26.3 BCM.

## Slide 7: National transmission system (NTS)
National Grid manages and operates the gas National Transmission System (NTS) in Great Britain, overseeing the daily balance of supply and demand.
The system includes around 4,760 miles of high-pressure pipelines and 618 above-ground facilities.
Gas is then conveyed through several stages of pressure reduction before reaching end users.

## Slide 8: Ranges of gas pressure
Intermediate pressure mains function within a range of 2 to 7 bar and are made from steel or polyethylene pipes.
Medium pressure mains operate between 75 mbar and 2 bar, using steel, polyethylene, cast iron, or ductile iron pipes.
Low pressure mains typically range from 30 mbar to 75 mbar and are constructed from polyethylene, cast iron, or ductile iron pipes.
High pressure supplies from nearby sources can reach pressures of up to 69 bar!

## Slide 9: Pressure regulation
When gas is transported from the source at high pressure, it is subsequently reduced to medium or intermediate pressures. These levels are typically delivered to larger industrial users.
For typical domestic and commercial uses, the pressure is further lowered at regulating stations.

## Slide 10: Storage
The UK has a network of natural gas storage facilities, with the largest being the Rough facility off the coast of East Yorkshire.
These facilities play a vital role in ensuring energy security by storing gas during periods of low demand and releasing it when needed, especially during winter peaks.
However, the UK's gas storage capacity is relatively low compared to other European countries.

## Slide 11: Storage
Rough facility:
The Rough facility, owned by Centrica, is the largest in the UK and can store a significant amount of gas. It was reopened in 2022 after being closed in 2017.
Capacity:
The UK's gas storage capacity is around 3.2 billion cubic meters, which is considerably less than countries like Germany and the Netherlands.

## Slide 12: Storage
Storage types:
Gas is stored in various facilities, including salt cavities and depleted gas reservoirs, with salt caverns being a common and relatively safe method according to the Health and Safety Executive.
Strategic importance:
Gas storage is crucial for energy security, allowing the UK to manage supply fluctuations and meet peak winter demand.

## Slide 13: Storage
Challenges:
The UK has faced criticism for having relatively low gas storage levels compared to other European nations.
Future plans:
There are ongoing discussions and plans to expand and optimise existing storage facilities like Rough and potentially develop new hydrogen storage sites.

## Slide 14: Supply infrastructure
Natural gas travels through a sophisticated distribution network before reaching properties:
Transmitted via low-pressure gas mains (≤75 mbar).
Distributed through polyethylene (PE) or steel pipework.
Terminates at property boundary in meter boxes or internal meter points.
Maintained at approximately 21 mbar nominal working pressure in domestic settings.

## Slide 15: Key components of NG installations
Component | Purpose | Installation requirements
Emergency Control Valve (ECV) | Isolates gas supply in emergencies. | Must be within 1m of meter, accessible, visible.
Meter | Measures gas usage (diaphragm meters common). | Secure mounting, correct orientation, sealed connections.
Regulator | Reduces incoming pressure to safe level. | Matched to meter capacity, correctly orientated.
Pipe Entry Sleeve | Prevents damage to building fabric. | Sealed, non-combustible material, appropriate diameter.
Labels & Signage | Warn others of live gas system. | Clear, permanent, positioned at key points.

## Slide 16: Location requirements
Meter installation requirements
Accessible at all times for emergency isolation and reading.
Well ventilated to prevent gas accumulation.
Not located near electrical intakes (minimum 150mm separation).
Protected from mechanical damage and environmental factors.
Secured to a solid structure capable of supporting weight.

## Slide 17: Location requirements
ECV specifications
Located within 1 metre of the meter.
Clearly visible at all times.
Properly labelled with “Gas Emergency Control”.
Quarter-turn operation with clear open/closed positions.
Free from obstruction by furniture or fixtures.

## Slide 18: Location requirements
Pipework requirements
Sleeved through walls with appropriate sealing.
Adequately clipped at specified intervals.
Free from obstruction and accessible for inspection.
Protected from corrosion and physical damage.
Traceable if buried (marker tape or detection wire).

## Slide 19: Frequently encountered issues
Inaccessible ECVs hidden behind appliances or fixtures.
Meters boxed in or concealed behind kitchen units.
Incorrect regulator fitted for the installation type.
Missing or illegible warning labels and signage.
Pipes buried in walls without proper sleeving or traceability.
Absent or incorrect gas bonding connections.
Inadequate ventilation around meter installations.

## Slide 20: Summary
You should now be able to:
Describe how Natural Gas is stored and supplied to domestic and light commercial premises.
Identify the correct layout and equipment involved in NG installations (meters, ECVs, pipe entry).
Explain how to ensure safe access, ventilation, and compliance with regulations.
Evaluate risks and non-compliances in NG meter and supply arrangements.

## Slide 21
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.