## Slide 1
Occupational Specialism: Gas Engineering
K1.27 Cleaning of components without compromising the
system and associated tools, equipment and materials
PowerPoint 1.27a: Cleaning principles, tools and system integrity

## Slide 2: Starter
Aadil uses a wire brush to clean a heat exchanger during a boiler service. He notices flakes coming off but puts the cover back on and relights the appliance. The boiler locks out later that week.
What mistakes did Aadil make?
What damage could occur from using the wrong tool?
What guidance should he have followed?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify tools, equipment, and materials used for cleaning gas appliance components.
Describe safe and effective cleaning techniques based on component type.
Explain how to follow the manufacturer’s instructions and servicing schedules.
Evaluate the risks of incorrect cleaning and how to prevent damage or unsafe operation.

## Slide 4: Why clean gas appliance components?
Regular cleaning of gas appliance components is not merely a maintenance formality – it's a critical safety practice that directly impacts appliance performance, efficiency, and longevity.
Beyond compliance with regulatory requirements, proper cleaning helps identify potential issues before they develop into serious faults.

## Slide 5: Why clean gas appliance components?
Dust, debris, and combustion deposits can significantly impair an appliance's operation, leading to reduced efficiency or potentially dangerous conditions.
When combustion surfaces become contaminated, the air-to-fuel ratio is affected, which can lead to incomplete combustion and the production of carbon monoxide.

## Slide 6: Why clean gas appliance components?
Ensure safe combustion and performance
Clean components maintain proper air-fuel ratios, flame patterns, and combustion efficiency, preventing production of harmful by-products like carbon monoxide.
Prevent operational issues
Regular cleaning prevents blockages in gas jets, sooting on heat exchangers, and faults in flame supervision devices and sensors.

## Slide 7: Why clean gas appliance components?
Support energy efficiency
Clean heat transfer surfaces maximise thermal efficiency, reducing fuel consumption and carbon emissions while lowering running costs.
Detect component deterioration
The cleaning process provides an opportunity to inspect for signs of wear, corrosion, or damage that might require further action.

## Slide 8: Tools and equipment for cleaning
Selecting the appropriate tools for cleaning gas appliance components is essential for effective maintenance without causing damage.
Each tool has specific applications and limitations that must be understood before use.

## Slide 9: Tools and equipment for cleaning
Tool/equipment | Appropriate use | Limitations/precautions
Soft-bristle brush | Burner head, electrode, casing interior | Avoid using on delicate surfaces; ensure bristles don't shed
Non-abrasive pad | Heat exchangers, electrodes | Never use steel wool or abrasive scourers
Combustion analyser | Pre/post cleaning performance check | Must be calibrated and in good working order
Lint-free cloth | Wipe surfaces without leaving fibres | Replace when soiled; ordinary cloths may leave debris
Vacuum with brush nozzle | Chamber and burner debris removal | Ensure nozzle is clean and doesn't scratch surfaces
Torch / mirror | Visual inspection before and after cleaning | Ensure sufficient illumination of all areas
Plastic scraper | Removing stubborn deposits | Never use metal scrapers on aluminium components
Digital camera / smartphone | Document component positioning before disassembly | Ensure images are clear enough to guide reassembly

## Slide 10: Tools and equipment for cleaning
Always inspect tools before use to ensure they're clean and in good condition.
Contaminated tools can transfer debris or chemicals between appliances, potentially causing cross-contamination issues.

## Slide 11: Cleaning products (MI-approved only)
The selection of cleaning products for gas appliance maintenance is strictly governed by Manufacturer’s Instructions (MI).
Using unapproved chemicals can damage components, compromise safety features, and potentially void warranties.
Always verify that cleaning products are explicitly approved for the specific appliance and component material.

## Slide 12: Cleaning products (MI-approved only)
Product type | Use area | Notes
Foam cleaner | Aluminium heat exchangers | Must be pH neutral to prevent corrosion.
Descaler | Condensate traps, plate heat exchangers | Must match MI concentration; never exceed recommended strength.
Degreaser (non-caustic) | Outer case, fan housing | Never use inside combustion area; can affect flame characteristics.
Electronic contact cleaner | PCB connections, sensor contacts | Must be non-conductive and quick-drying.
Stainless steel cleaner | Stainless steel heat exchangers | Avoid silicone-based products that may affect combustion.

## Slide 13: Cleaning products (MI-approved only)
Always ensure adequate ventilation when using cleaning chemicals, wear appropriate PPE as specified in the product's safety data sheet, and dispose of used cleaning materials according to local regulations and environmental guidelines.

## Slide 14: Risks of improper cleaning
Material damage
Using wire brushes on aluminium heat exchangers removes protective coatings, leading to accelerated corrosion and premature failure.
Similarly, aggressive chemical cleaners can degrade gaskets and seals, compromising the pressure integrity of the appliance.

## Slide 15: Risks of improper cleaning
Electrical faults
Water or cleaning solutions contacting electrical terminals can cause short circuits, PCB failures, or damage to sensitive electronic components.
Even residual moisture can lead to corrosion of contacts and intermittent faults that are difficult to diagnose.

## Slide 16: Risks of improper cleaning
Component degradation
Using inappropriate solvents on plastic components can cause material degradation, warping, or embrittlement.
This is particularly concerning for flue components where structural integrity is critical for safe operation.

## Slide 17: Risks of improper cleaning
Operational hazards
Failure to properly check appliance operation after cleaning can leave issues undetected.
Burner misalignment, incomplete seals, or debris left in critical pathways can lead to dangerous operating conditions, including carbon monoxide production.
The consequences of improper cleaning extend beyond immediate component damage – they can create dangerous situations for occupants and lead to expensive repairs or appliance replacement.

## Slide 18: Case study: heat exchanger cleaning gone wrong
A gas engineer attempted to clean a condensing boiler heat exchanger using a wire brush after finding it partially blocked with combustion deposits.
The customer reported the boiler was making unusual noises and shutting down frequently within weeks of the service.

## Slide 19: Case study: heat exchanger cleaning gone wrong
Investigation findings
Severe flaking of the protective coating on aluminium heat exchanger surfaces.
Early signs of corrosion in areas where coating was removed.
Loose material had partially blocked the condensate trap.
Water leakage at heat exchanger joints due to gasket damage during reassembly.

## Slide 20: Case study: heat exchanger cleaning gone wrong
Outcome
The heat exchanger required complete replacement at a cost of £450, plus additional labour charges.
The warranty was invalidated due to improper servicing techniques, leaving the customer to bear the full cost.

## Slide 21: Manufacturer's Instructions (MI)
Access manufacturer documentation
Before beginning any cleaning operation, obtain and thoroughly review the manufacturer's servicing instructions specific to the appliance model.
These documents are legally binding and must be followed to maintain warranty and ensure safety compliance.

## Slide 22: Manufacturer's Instructions (MI)
Identify specified cleaning methods
MI will specify exactly what components can be cleaned, which tools and products are approved, and the correct procedures to follow.
Any deviation from these instructions may constitute improper maintenance.

## Slide 23: Manufacturer's Instructions (MI)
Follow disassembly sequence
The correct order for removing components is critical to prevent damage.
Document or photograph positions before disassembly to ensure accurate reassembly.
Handle seals and gaskets with particular care.

## Slide 24: Manufacturer's Instructions (MI)
Perform required post-cleaning checks
After cleaning, MI will specify essential checks such as flame picture assessment, combustion analysis, or pressure testing. These verify the appliance is operating safely and efficiently following maintenance.
Remember that the manufacturer's instructions take precedence over general industry practices. What may be acceptable for one appliance model could cause damage to another due to differences in materials, design, or operational parameters.

## Slide 25: Cleaning main heat exchangers
Heat exchangers are critical components that transfer heat from the combustion process to the water circulating through the heating system.
Due to their constant exposure to both combustion products and water, they're particularly vulnerable to both fouling and corrosion.
The cleaning approach must be tailored to the specific material of construction.

## Slide 26: Cleaning main heat exchangers
Most modern condensing boilers use aluminium or stainless steel heat exchangers, each requiring different cleaning methods to prevent damage.
Always remove the heat exchanger according to manufacturer's instructions rather than attempting to clean in situ, as this ensures thorough cleaning access and prevents cleaning agents from contacting sensitive electronic components.

## Slide 27: Cleaning main heat exchangers
Material | Approved method | Never use
Aluminium | pH-neutral foam cleaner, soft brush | Wire brushes, acidic cleaners
Stainless steel | Manufacturer-approved descaler, non-abrasive pad | Chloride-containing cleaners
Copper | Specific copper-safe descaler, soft brush | Ammonia-based products

## Slide 28: Burner cleaning techniques
Atmospheric burners
Remove burner assembly according to MI
Inspect for cracks, warping, or distortion
Clear gas ports using compressed air (never wire)
Use a soft brush to remove loose deposits
Vacuum debris with care not to damage ports
Check the injector is clear using an appropriate size tool

## Slide 29: Burner cleaning techniques
Pre-mix burners
Extreme care required due to surface perforations
Inspect mesh/gauze for damage or deterioration
Use only a soft brush or vacuum for surface deposits
Never attempt to clear individual holes
Replace if significantly blocked or damaged
Check the venturi is clear of obstructions

## Slide 30: Burner cleaning techniques
Post-cleaning verification
Check all connections for gas-tightness
Verify flame appearance is correct (even blue flame)
Perform combustion analysis to confirm proper operation
Check for correct gas pressure and gas rate
Ensure no unusual noises during operation

## Slide 31: Burner cleaning techniques
Improper burner cleaning is a leading cause of combustion issues.
Even minor damage to burner surfaces can significantly alter the combustion characteristics, potentially leading to incomplete combustion and carbon monoxide production.
Always document the condition of burners before and after cleaning.

## Slide 32: Cleaning flame sensing devices
Flame sensing devices are critical safety components that verify the presence of a flame during appliance operation.
If these components become contaminated, they may fail to detect the flame correctly, causing the appliance to shut down unnecessarily or, more dangerously, fail to shut down when the flame is absent.

## Slide 33: Cleaning flame sensing devices
Cleaning process for flame sensors
Isolate the electrical supply and allow it to cool completely
Remove sensor according to manufacturer's instructions
Document original position and orientation
Gently clean the sensing element with fine emery cloth or a non-abrasive pad
Avoid touching the sensing element with bare fingers
Refit to the exact original position, checking gap specifications
Test operation through multiple on/off cycles

## Slide 34: Cleaning flame sensing devices
Critical safety note
Never attempt to bend flame detection electrodes to adjust position unless specifically instructed by the manufacturer.
The ceramic insulation is brittle and can crack internally, creating a potential safety hazard that may not be immediately visible.

## Slide 35: Cleaning flame sensing devices
For thermocouples and thermophiles, cleaning should be limited to gentle wiping with a clean, lint-free cloth.
Any abrasive cleaning can damage the thin metal sheath and affect the device's ability to generate the millivolt signal required for safe operation.

## Slide 36: Cleaning condensate systems
Condensing boilers produce acidic condensate (pH 3.5-5) as a by-product of the combustion process.
This condensate must be properly managed and drained from the appliance through the condensate system.
Blockages in this system are a common cause of winter breakdowns and can lead to water damage or appliance lockouts.

## Slide 37: Cleaning condensate systems
Safety preparation
Isolate both electrical and gas supplies before beginning work. Have appropriate containers ready to collect potentially contaminated water. Wear gloves to protect against acidic condensate.
Trap removal
Follow MI to correctly remove the condensate trap. Note the orientation of components and take photographs if necessary. Be prepared for water spillage during removal.

## Slide 38: Cleaning condensate systems
Cleaning process
Disassemble the trap according to MI and flush with clean water to remove sludge and deposits. If permitted by the manufacturer, check for and remove any limescale buildup using an approved descaler.
System inspection
Inspect all condensate pipework for damage, proper fall (minimum 3°) and appropriate sizing. Check external runs for proper insulation where freezing could occur.

## Slide 39: Cleaning condensate systems
Reassembly and testing
Reassemble the trap, ensuring all seals are correctly positioned. Prime with clean water before reconnection. Test the system by running the appliance and verifying proper drainage.

## Slide 40: Cleaning fan assemblies
Importance of fan maintenance
Fans in modern gas appliances serve critical functions related to both combustion and safety.
They provide primary air for combustion in fan-assisted appliances and evacuate combustion products in room-sealed systems.
Dust accumulation on fan blades can cause imbalance, reducing efficiency and creating noise, while debris can completely obstruct airflow.

## Slide 41: Cleaning fan assemblies
Access and removal
Always follow the manufacturer's sequence for fan removal. Document cable connections before disconnecting and handle the assembly with care to avoid damaging the impeller or motor.
Some manufacturers specify that fans should not be removed except for replacement, so verify this before proceeding.

## Slide 42: Cleaning fan assemblies
Cleaning methods
Use a soft brush or vacuum to remove loose dust and debris
Check the impeller can rotate freely with no obstructions
Inspect for signs of heat damage or warping
Clean pressure-sensing tubes with compressed air if present
Never immerse the fan motor in water or cleaning solutions
Avoid excessive force on plastic impeller blades

## Slide 43: Cleaning fan assemblies
Never attempt to lubricate fan bearings unless specifically instructed by the manufacturer.
Most modern fans use sealed bearings that can be damaged by additional lubrication.

## Slide 44: Cleaning different flue systems
Open flued appliances
These appliances draw combustion air from the room and expel products via a flue.
Inspect the draught diverter for debris and blockages
Check flue integrity throughout accessible length
Verify proper updraught using smoke match test
Clean flue ways according to manufacturer's guidelines
Ensure spillage detection devices are clean and functional

## Slide 45: Cleaning different flue systems
Room-sealed appliances
These draw air from outside and expel combustion products without interaction with room air.
Inspect the terminal for obstructions or damage
Check internal flue seals for integrity
Clean fan chamber and pressure sensing ports
Verify correct operation of pressure switches
Ensure condensate drain paths are clear if applicable

## Slide 46: Cleaning different flue systems
Balanced flue appliances
These use a concentric flue system with inner and outer passageways.
Inspect both inner and outer flue tubes for obstructions
Check sealing gaskets between concentric components
Verify correct air flow through both passageways
Clean terminal guard to ensure unrestricted flow
Look for evidence of water ingress at joints

## Slide 47: Cleaning gas controls and valves
Gas control valves are precision components that regulate the flow of gas to the appliance.
They should be handled with extreme care during cleaning, as improper techniques can lead to gas leaks or control failure.

## Slide 48: Cleaning gas controls and valves
Cleaning limitations
Unlike other components, internal cleaning of gas valves is generally prohibited.
Manufacturer's instructions typically limit maintenance to external dusting and inspection.
Any attempt to disassemble or internally clean gas valves voids warranties and may create a safety hazard.

## Slide 49: Cleaning gas controls and valves
External cleaning
Use dry, lint-free cloth to remove dust from exterior surfaces
Carefully clean around electrical connections without disturbing them
Inspect for signs of corrosion, heat damage, or distortion
Check all connections for evidence of gas leakage

## Slide 50: Cleaning gas controls and valves
Critical safety information
Never use cleaning solvents, water, or compressed air on gas valves or controls.
These can enter the valve mechanism and cause corrosion or contamination of internal components, leading to failure of safety functions.

## Slide 51: Cleaning gas controls and valves
If a gas valve is suspected to be faulty or contaminated internally, the only safe solution is replacement with an appropriate manufacturer-approved part.
Attempting repairs or internal cleaning creates significant safety risks and is not permitted under Gas Safety regulations.

## Slide 52: Cleaning considerations for different appliance types
Boilers
Focus on heat exchanger and burner cleaning
Check pump filter for debris
Clean condensate system thoroughly
Verify pressure relief valve operation

## Slide 53: Cleaning considerations for different appliance types
Gas fires
Clean decorative fuel effects per MI
Check pilot assembly for blockages
Verify glass panel seals after cleaning
Inspect catalyst if fitted

## Slide 54: Cleaning considerations for different appliance types
Cookers
Clean burner caps and hob injectors
Check oven burner for debris
Verify door seals for cleanliness
Clean flame supervision devices

## Slide 55: Cleaning considerations for different appliance types
Water heaters
Descale heat exchangers if permitted
Clean water filters and flow sensors
Check diaphragm operation in instantaneous units
Verify temperature limiting devices

## Slide 56: Cleaning considerations for different appliance types
Each appliance type presents unique cleaning challenges based on its design, function, and operating environment.
Always consult the specific manufacturer's instructions for the particular model you are servicing, as cleaning requirements can vary significantly between different manufacturers and even between models from the same manufacturer.

## Slide 57: The impact of environmental factors on cleaning requirements
High humidity environments
Appliances in environments with high humidity, such as kitchens or bathrooms, may require more frequent cleaning due to accelerated corrosion and condensation issues.

## Slide 58: The impact of environmental factors on cleaning requirements
High humidity environments
Pay particular attention to:
Electrical connections for signs of corrosion
PCB housings for evidence of moisture ingress
Increased limescale formation in water-carrying components
More rapid accumulation of dust that becomes damp and adheres to surfaces

## Slide 59: The impact of environmental factors on cleaning requirements
Dusty environments
Locations with high dust levels, such as properties near construction sites or industrial areas, present unique challenges:
Air filters may require more frequent cleaning or replacement
Fan assemblies can become imbalanced due to uneven dust accumulation
Burner ports may become blocked more quickly
Flame supervision devices may fail prematurely due to contamination

## Slide 60: The impact of environmental factors on cleaning requirements
Hard water areas
Appliances in hard water regions require special attention to limescale-related issues:
Heat exchangers may require approved descaling treatments
Condensate traps can become blocked more frequently
Water flow sensors may become less responsive
Plate heat exchangers in combi boilers often require more frequent cleaning

## Slide 61: The impact of environmental factors on cleaning requirements
When servicing appliances, always consider the specific environmental conditions in which they operate.
Cleaning schedules and methods may need to be adjusted accordingly, with some environments necessitating more frequent servicing than the standard annual recommendation.

## Slide 62: System integrity: reassembly and verification
Correct reassembly sequence
Follow the manufacturer's instructions precisely for reassembly order.
Use any reference photos taken during disassembly to ensure components are replaced in exactly the same orientation.
Pay particular attention to sealing faces and gasket positioning.

## Slide 63: System integrity: reassembly and verification
Seal integrity
Replace any seals or gaskets that show signs of damage or deterioration.
Never reuse one-time seals such as fibre washers or O-rings.
Ensure all sealing surfaces are clean and free from debris before reassembly.

## Slide 64: System integrity: reassembly and verification
Correct torque application
Use appropriate torque settings when tightening fasteners.
Over-tightening can damage components or crush seals, while under-tightening can lead to leaks.
Follow the manufacturer's specifications for torque values where provided.

## Slide 65: System integrity: reassembly and verification
Visual inspection
Before final closure, perform a thorough visual inspection of all cleaned components and connections.
Check for any tools, debris, or loose parts that may have been inadvertently left inside the appliance.

## Slide 66: System integrity: reassembly and verification
Functional testing
Perform comprehensive testing after reassembly, including gas tightness testing of all disturbed joints, combustion analysis, and operational checks through multiple cycles to ensure consistent performance.

## Slide 67: Documentation and record keeping
Proper documentation is not just good practice; it's a legal requirement under Gas Safety (Installation and Use) Regulations.
Comprehensive records protect both the engineer and the customer by providing evidence of work completed and the condition of the appliance.

## Slide 68: Documentation and record keeping
Required documentation
Details of all components cleaned, and methods used
Before and after combustion readings where applicable
Parts replaced and reasons for replacement
Any advice given to the customer regarding appliance condition
Recommendations for future maintenance or repairs
Evidence of safety checks performed after cleaning

## Slide 69: Documentation and record keeping
Benefits of thorough records
Provides historical data for future reference
Helps identify developing issues over time
Serves as evidence in case of disputes
Demonstrates a professional approach to customers
Aids in the diagnosis of intermittent faults
Complies with legal obligations under GSIUR

## Slide 70: Documentation and record keeping
Modern record-keeping often combines traditional paperwork with digital documentation.
Many engineers now take before and after photographs as additional evidence of work completed and to assist with future servicing.

## Slide 71: Handling cleaning waste responsibly
The cleaning of gas appliances generates various waste materials that must be handled and disposed of appropriately.
Improper disposal can lead to environmental damage, health risks, and potential legal consequences.

## Slide 72: Handling cleaning waste responsibly
Chemical waste
Never pour cleaning chemicals down domestic drains
Collect used cleaning solutions in appropriate containers
Follow the manufacturer's instructions for neutralising before disposal
Transport to approved waste handling facilities
Retain records of hazardous waste disposal as required by regulations

## Slide 73: Handling cleaning waste responsibly
Combustion deposits
Collect soot and debris in sealed bags to prevent dispersion
Be aware that deposits may contain hazardous compounds
Never dispose of in standard household waste
Consider deposits from older appliances may contain asbestos
If asbestos is suspected, follow specific handling protocols

## Slide 74: Handling cleaning waste responsibly
Recyclable materials
Segregate metal components for recycling
Clean packaging from replacement parts should be recycled
Used non-hazardous cleaning cloths can often be washed and reused
Electronic components contain valuable recoverable materials
Always follow local authority guidelines for recycling

## Slide 75: Troubleshooting common cleaning-related issues
Problem | Possible causes | Diagnostic steps | Preventive measures
Appliance locks out after cleaning | Disturbed electrical connections, misaligned components | Check all connections, verify flame sensor positioning, review error codes. | Document precise component positions before disassembly, use care when handling connectors.
Unusual noise after cleaning | Loose components, improper reassembly, foreign objects | Listen for location of noise, inspect suspect areas, check all fasteners. | Use methodical reassembly process, count fasteners to ensure none are missed.
Water leaks following service | Damaged seals, overtightened connections, incorrect assembly | Inspect all water-carrying components, check gasket seating, verify correct parts used. | Replace rather than reuse seals, follow torque specifications, check for proper alignment.
Poor combustion readings | Incomplete cleaning, damaged components, incorrect settings | Recheck burner and heat exchanger, verify gas pressure, check air supply. | Perform thorough cleaning following MI, verify operation with combustion analyser.
Controls malfunctioning | Moisture ingress, static damage, contamination | Check for water damage, verify connections, inspect for cleaning residue. | Protect electronic components during cleaning, avoid water near controls.

## Slide 76: Summary
You should now be able to:
Identify tools, equipment, and materials used for cleaning gas appliance components.
Describe safe and effective cleaning techniques based on component type.
Explain how to follow the manufacturer’s instructions and servicing schedules.
Evaluate the risks of incorrect cleaning and how to prevent damage or unsafe operation.

## Slide 77
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.