## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.15 Types of control systems

## Slide 2: Introduction / starter
Warm-up
Why can a well-installed heat pump still be expensive to run?
Pair-share
Name three controls a customer might interact with.
Discuss
"Controls turn design intent into real performance."
Notes: Stop point: 3–5 minute discussion. Draw out thermostat, programmer/schedule, weather compensation, TRVs, app, DHW boost, hybrid controls and time-of-use tariffs.

## Slide 3: Objectives
Foundations
Identify common control systems for low carbon heating
Describe characteristics, operation, and suitability
Performance
Explain how controls support comfort and efficiency
Ensure regulatory and scheme compliance
Digital and Future
Recognise digital controls, apps, and remote monitoring
Link selection to budget and future scalability
Notes: Learners should be able to choose suitable controls for a scenario and explain why, rather than simply name control types.
Advanced strategies and readiness
Explain hot water priority, hybrid control, tariffs, and smart grid readiness.

## Slide 4: Why controls matter in low carbon systems
Efficiency and Stability
Steady operation
Heat pumps thrive on longer periods at lower flow temperatures. Avoid frequent cycling.
Weather compensation
Keeps flow temperatures as low as practical to improve CoP.
Demand management
Strategic coordination
Manages heating, hot water, and zone supply to ensure design intent meets performance.
Comfort control
Maintains steady room temperatures and reliable DHW recovery.
Digital insights
Remote monitoring
Apps show fault codes, energy use, and performance trends for early issue detection.
Data-driven decisions
Supports better decision-making through visibility of schedules and trends.
Notes: Tutor note: Link to K1.17 low temperature heating and COP/SCOP. Controls do not fix poor design, but they help a good design operate efficiently.
Tutor example
A heat pump is installed correctly, but the customer turns the room thermostat up and down like they did with a gas boiler. They also switch the heating off overnight and use DHW boost every morning. The system then recovers from cold conditions, runs at higher flow temperatures, uses the immersion heater more often and costs more to run.
The issue is not necessarily the heat pump itself — it may be the control strategy and user operation. Correct handover would explain steady running, modest setbacks, weather compensation, DHW scheduling and when boost should be used.
Learner takeaway
Controls are the link between design and real-life performance. A good low carbon heating system needs the right controls, correct commissioning and clear user guidance so the system operates efficiently, comfortably and safely.
Prompt: What happens if a customer constantly overrides schedules or sets high flow temperatures?

## Slide 5: Why controls matter in low carbon systems
Risks of poor settings
Manual overrides and high setpoints cause short cycling.
Can lead to overheating, slow warm-up, and high running costs.
Mismatch with system design (e.g. TRVs) reduces active water volume.
Commissioning and Handover
Installer must record key settings and explain adjustable controls.
Customers need to understand holiday modes and defrost behaviour.
Identify which settings should never be changed by the user.
Notes: Tutor note: Link to K1.17 low temperature heating and COP/SCOP. Controls do not fix poor design, but they help a good design operate efficiently.
Tutor example
A heat pump is installed correctly, but the customer turns the room thermostat up and down like they did with a gas boiler. They also switch the heating off overnight and use DHW boost every morning. The system then recovers from cold conditions, runs at higher flow temperatures, uses the immersion heater more often and costs more to run.
The issue is not necessarily the heat pump itself — it may be the control strategy and user operation. Correct handover would explain steady running, modest setbacks, weather compensation, DHW scheduling and when boost should be used.
Learner takeaway
Controls are the link between design and real-life performance. A good low carbon heating system needs the right controls, correct commissioning and clear user guidance so the system operates efficiently, comfortably and safely.
Prompt: What happens if a customer constantly overrides schedules or sets high flow temperatures?

## Slide 6: Control system suitability: Decision factors
Efficiency goals
Lower flow temperatures, weather compensation, and reduced cycling to maximise system performance.
Budget and Tech
Balancing basic manual controls against advanced connected systems and smart automation.
Comfort and Access
Zoning, intuitive scheduling, remote access, and ensuring simplicity for the end user.
Future scalability
Consideration for PV integration, battery storage, dynamic tariffs, and smart grid/hybrid expansion.
Compatibility
Alignment between heat pump, cylinder, emitters, wiring, and communication protocols.
Compliance
Adherence to manufacturer instructions, Building Regulations, and providing MCS evidence.
Notes: Tutor depth:
Control choice should be justified. A high-tech control may be unsuitable if the customer cannot use it or the system is incompatible. A basic thermostat may be insufficient where weather compensation, DHW priority or tariff scheduling is needed.
Activity: learners rank factors for a customer on a tight budget vs. a customer with PV/battery and high comfort expectations.

## Slide 7: Thermostats: Characteristics and operation
Core function and types
Sensing and Demand
Measures air temp and sends heat demand below setpoint. Reaches target and removes demand.
Wired to Smart
Ranges from basic on/off to smart apps with learning and remote access.
Optimal operation
Heat pump dynamics
Works best with long periods and small adjustments. Avoid frequent manual overrides.
Weather compensation
Fine-tunes comfort while WC manages flow temp based on outdoor conditions.
Critical placement
Avoid interference
Keep away from sunlight, draughts, radiators, and fireplaces.
Impact of poor location
Causes incorrect readings, leading to overheating or energy waste.
Notes: Tutor note:
A thermostat is a simple control but can cause problems if poorly located or misunderstood. In low-temperature systems, changing the thermostat does not create instant heat like a high-temperature boiler might.
Tutor example
A customer installs a smart thermostat and frequently increases the room temperature by 4–5°C when they feel cold. The thermostat then calls for maximum heating demand, causing the heat pump to operate at higher flow temperatures and reducing efficiency.
A better approach is to leave the thermostat at a stable setpoint (e.g. 20–21°C), allow weather compensation to manage flow temperature, and use modest schedule adjustments where necessary.
Similarly, if the cylinder thermostat is incorrectly set too low, the customer may experience poor hot water availability. If set too high permanently, efficiency may reduce and running costs may increase.
Learner takeaway
Thermostats control comfort, but they also influence efficiency. For heat pump systems, room thermostats, cylinder thermostats and smart controls must work together with weather compensation, DHW controls and system design to provide comfortable, efficient and reliable operation.
Prompt: what could happen if a thermostat is placed near a radiator or in direct sunlight?

## Slide 8: Thermostats: Characteristics and operation
Hot water and hygiene (Cylinder thermostats)
Monitor stored water temp and signal HP for heating cycle.
Legionella Protection: Periodically raise temp to ~60°C for hygiene.
Balance efficiency with high demand and safety requirements.
Essential user handover
Customers must understand:
Adjusting room temp, schedules, and holiday mode.
Activating DHW boost and using mobile apps.
Why constant adjustments reduce HP efficiency.
Notes: Tutor note:
A thermostat is a simple control but can cause problems if poorly located or misunderstood. In low-temperature systems, changing the thermostat does not create instant heat like a high-temperature boiler might.
Tutor example
A customer installs a smart thermostat and frequently increases the room temperature by 4–5°C when they feel cold. The thermostat then calls for maximum heating demand, causing the heat pump to operate at higher flow temperatures and reducing efficiency.
A better approach is to leave the thermostat at a stable setpoint (e.g. 20–21°C), allow weather compensation to manage flow temperature, and use modest schedule adjustments where necessary.
Similarly, if the cylinder thermostat is incorrectly set too low, the customer may experience poor hot water availability. If set too high permanently, efficiency may reduce and running costs may increase.
Learner takeaway
Thermostats control comfort, but they also influence efficiency. For heat pump systems, room thermostats, cylinder thermostats and smart controls must work together with weather compensation, DHW controls and system design to provide comfortable, efficient and reliable operation.
Prompt: what could happen if a thermostat is placed near a radiator or in direct sunlight?

## Slide 9: Controllers: The system control centre
The system “brain"
Coordinates the whole low carbon heating system, linking heat pumps, pumps, valves, sensors, and emitters.
Crucial for efficient operation through steady control and coordinated demand.
Demand management
Manages space heating, domestic hot water (DHW), and modes like frost protection or backup.
Handles hot water priority by pausing heating for cylinder recovery.
Operational logic
Controls pumps and zones in sequence to avoid flow faults and short cycling.
Manages weather compensation to adjust flow temperatures, based on outdoor conditions.
Notes: Tutor depth:
The controller is where system logic lives. Incorrect controller settings can create high energy use, poor comfort or faults. Learners should know where to find settings but respect competence boundaries and password-protected/service menus.
Tutor example
An ASHP is installed with radiators, a hot water cylinder and two heating zones. The controller is set up incorrectly, so the heat pump receives a demand before the zone valve fully opens. The heat pump starts, flow is restricted, and the system records a flow fault.
The issue is not the heat pump unit itself — it is the control sequence. Correct commissioning would check the order of operation: thermostat demand → zone valve opens → pump runs → heat pump enabled → flow confirmed.
Learner takeaway
The controller links the whole system together. For heat pumps, correct controller setup is essential for comfort, efficiency, hot water recovery, safety, diagnostics and long-term reliability.
Stop point: identify which settings should be user-facing vs. installer-only.

## Slide 10: Controllers: The system control centre
Diagnostics and Configuration
Displays fault codes, live data, and operating modes for troubleshooting.
Installer settings (e.g. flow temps, curves) must be protected from inappropriate changes.
Commissioning and Handover
Setup must match system design and hydraulic layout.
Record all key setpoints and installer parameters to create a service baseline.
Notes: Tutor depth:
The controller is where system logic lives. Incorrect controller settings can create high energy use, poor comfort or faults. Learners should know where to find settings but respect competence boundaries and password-protected/service menus.
Tutor example
An ASHP is installed with radiators, a hot water cylinder and two heating zones. The controller is set up incorrectly, so the heat pump receives a demand before the zone valve fully opens. The heat pump starts, flow is restricted, and the system records a flow fault.
The issue is not the heat pump unit itself — it is the control sequence. Correct commissioning would check the order of operation: thermostat demand → zone valve opens → pump runs → heat pump enabled → flow confirmed.
Learner takeaway
The controller links the whole system together. For heat pumps, correct controller setup is essential for comfort, efficiency, hot water recovery, safety, diagnostics and long-term reliability.
Stop point: identify which settings should be user-facing vs. installer-only.

## Slide 11
Weather compensation
Dynamic heating adjustment
Adjusts heating flow temperature based on outdoor temperature using a sensor, avoiding fixed high-temperature operation to match weather conditions.
Temperature logic
Colder outside = Higher flow
Increases temp to maintain comfort as building loses heat faster.
Milder outside = Lower flow
Reduces flow temp to improve efficiency and avoid overheating.
Operational efficiency
Minimal temperature lift
Keeps flow as low as practical to improve CoP and reduce running costs.
Emitters and stability
Most effective with correctly sized low-temp emitters and stable running patterns.
Notes: Tutor example:
If it is mild outside, the system may only need low flow temperatures to maintain comfort. Weather compensation reduces compressor work and improves COP. If the curve is set too steep, the system may run hotter than necessary.
Tutor example
A weather sensor is fitted on a south-facing wall in direct sunlight. On a cold but sunny winter morning, the sensor reads warmer than the true outdoor air temperature. The controller thinks the building needs less heat, so it lowers the flow temperature. The customer then complains that the house feels cold.
Correct approach: locate the sensor according to manufacturer instructions, usually on a shaded north or north-west-facing wall, then set and fine-tune the compensation curve during commissioning and early operation.
Learner takeaway
Weather compensation helps the heat pump run only as hot as needed. Correct sensor location and curve setup are essential. A poor sensor position can make the controller “think” the weather is different from reality, causing poor comfort or wasted energy.
Learner question: why is sensor location important?

## Slide 12
Weather compensation
Correct sensor placement
Optimal location
North or north-west facing wall; away from direct sunlight and heat sources.
Avoid interference
Keep clear of vents, flues, and warm air discharge points.
The Compensation Curve
Defines the flow temp relationship to outdoor temp changes.
Too high: System runs hotter than needed, increasing costs.
Too low: Customer may experience under-heating in cold weather.
Poor setup risks
Incorrect sensor position or curve settings can lead to:
Under-heating or overheating
Short cycling and high flow temperatures
Loss of customer confidence
Notes: Tutor example:
If it is mild outside, the system may only need low flow temperatures to maintain comfort. Weather compensation reduces compressor work and improves COP. If the curve is set too steep, the system may run hotter than necessary.
Tutor example
A weather sensor is fitted on a south-facing wall in direct sunlight. On a cold but sunny winter morning, the sensor reads warmer than the true outdoor air temperature. The controller thinks the building needs less heat, so it lowers the flow temperature. The customer then complains that the house feels cold.
Correct approach: locate the sensor according to manufacturer instructions, usually on a shaded north or north-west-facing wall, then set and fine-tune the compensation curve during commissioning and early operation.
Learner takeaway
Weather compensation helps the heat pump run only as hot as needed. Correct sensor location and curve setup are essential. A poor sensor position can make the controller “think” the weather is different from reality, causing poor comfort or wasted energy.
Learner question: why is sensor location important?

## Slide 13: Optimisation and adaptive control
Intelligent heating initiation
Calculates start times based on building thermal performance to reach comfort targets precisely when needed, rather than using fixed schedules.
System benefits
Reduced energy waste
Prevents early or excessive heating by matching run time to actual demand.
Enhanced comfort
Ensures desired temperatures are achieved exactly at the occupancy time.
Adaptive intelligence
Data integration
Utilises indoor/outdoor temps, previous warm-up history, and occupancy patterns.
Machine learning
Controls "learn" building behaviour over time for improved accuracy.
Heat pump compatibility
Steady operation
Supports gradual recovery, avoiding aggressive and
inefficient temperature boosts.
Control harmony
Works alongside weather compensation and zoning to maintain stability.
Notes: Tutor note:
Optimisation is not the same as simple time scheduling. It aims to meet comfort at the required time with less waste. However, poor setup or user overrides can undermine it.
Tutor example
A customer wants the living room at 20°C by 7:00am. With a basic timer, the heating might switch on at 6:30am, but on cold mornings the room may still be too cool. The customer then raises the thermostat or increases the flow temperature, reducing efficiency.
With optimisation enabled, the controller may learn that on colder mornings it needs to start earlier, for example at 5:45am, while on milder mornings it may start later. The aim is steady heat pump operation and comfort by 7:00am without unnecessary high-temperature boosting.
Learner takeaway
Optimisation helps the heat pump plan ahead. It supports comfort by allowing gradual warm-up, while protecting efficiency by avoiding unnecessary run time, excessive flow temperatures and repeated manual overrides.
Prompt: how might optimisation help a heat pump system compared with a simple on/off timer?

## Slide 14: Optimisation and adaptive control
Suitability and Application
Optimal for properties with regular, predictable occupancy schedules.
Less effective with irregular use or poor building fabric performance.
Efficiency is compromised by frequent manual overrides.
Commissioning and Handover
Installer must enable and calibrate according to manufacturer design intent.
Customer education:
Explain that systems may start earlier than scheduled to ensure comfort at the set time.
Notes: Tutor note:
Optimisation is not the same as simple time scheduling. It aims to meet comfort at the required time with less waste. However, poor setup or user overrides can undermine it.
Tutor example
A customer wants the living room at 20°C by 7:00am. With a basic timer, the heating might switch on at 6:30am, but on cold mornings the room may still be too cool. The customer then raises the thermostat or increases the flow temperature, reducing efficiency.
With optimisation enabled, the controller may learn that on colder mornings it needs to start earlier, for example at 5:45am, while on milder mornings it may start later. The aim is steady heat pump operation and comfort by 7:00am without unnecessary high-temperature boosting.
Learner takeaway
Optimisation helps the heat pump plan ahead. It supports comfort by allowing gradual warm-up, while protecting efficiency by avoiding unnecessary run time, excessive flow temperatures and repeated manual overrides.
Prompt: how might optimisation help a heat pump system compared with a simple on/off timer?

## Slide 15
Scheduling and set-backs
Core concepts: Targets and setbacks
A schedule sets when heating and DHW targets apply (e.g. comfort in morning/evening). A set-back reduces temperature instead of switching off, maintaining a background level.
Heat pump operation
Small setbacks
Suits steady operation using low flow temps. Reducing by a few degrees avoids long recovery.
Deep setback risks
Can lead to longer warm-ups, backup heater use, and increased running costs.
Underfloor heating (UFH)
Thermal mass
Responds slowly; set-backs maintain background slab temperature.
Steadier comfort
Prevents heating up from completely cold daily, avoiding aggressive warm-ups.
DHW scheduling
Demand matching
Set around expected use (showers/baths) and hygiene (anti-Legionella).
Tariff strategy
Consider off-peak rates, PV generation, or battery storage.
Notes: Tutor depth:
Set-back is a key concept. In many heat pump systems, turning heating fully off can make recovery slow and inefficient. A modest set-back may preserve comfort while saving energy.
Tutor example
A home has underfloor heating downstairs. The customer turns the heating fully off overnight, and every morning the floor has to warm from cold. Because UFH responds slowly, the room is still cool at breakfast time, so the customer raises the thermostat and complains the system is slow.
A better strategy is to use a modest overnight set-back. The floor remains gently warm, the heat pump can recover gradually, and comfort is achieved without needing high flow temperatures or excessive boost.
Learner takeaway
Set-back is not the same as switching off. For heat pumps and underfloor heating, a controlled lower temperature often supports better comfort and efficiency than letting the building or floor cool completely every day.
Scenario: customer sets heating off overnight then complains rooms are cold at 7am. What control advice might be needed?

## Slide 16
Scheduling and set-backs
Building and routine alignment
Insulated homes hold heat well and need only small set-backs.
High heat-loss homes cool quickly and need careful scheduling.
Controls must match the specific building fabric and occupancy.
User guidance essentials
Customers must understand heat pumps aren't "on/off" boilers.
Key training points:
Explain set-back vs. off, and holiday modes.
Why constant manual overrides increase costs.
Notes: Tutor depth:
Set-back is a key concept. In many heat pump systems, turning heating fully off can make recovery slow and inefficient. A modest set-back may preserve comfort while saving energy.
Tutor example
A home has underfloor heating downstairs. The customer turns the heating fully off overnight, and every morning the floor has to warm from cold. Because UFH responds slowly, the room is still cool at breakfast time, so the customer raises the thermostat and complains the system is slow.
A better strategy is to use a modest overnight set-back. The floor remains gently warm, the heat pump can recover gradually, and comfort is achieved without needing high flow temperatures or excessive boost.
Learner takeaway
Set-back is not the same as switching off. For heat pumps and underfloor heating, a controlled lower temperature often supports better comfort and efficiency than letting the building or floor cool completely every day.
Scenario: customer sets heating off overnight then complains rooms are cold at 7am. What control advice might be needed?

## Slide 17: Hot water priority
Operational priority
Temporarily prioritises cylinder/DHW heating over space heating to ensure rapid recovery of domestic hot water supplies.
System impact
Heating recovery
Ensures hot water recovery but may pause or reduce space heating during the process.
DHW demand
Critical when demand is high or cylinder recovery is slower than a traditional boiler.
Performance and strategy
Boost mechanisms
Can involve higher flow temperatures and immersion/backup boost if required.
Scheduling logic
Align DHW schedules with usage patterns, hygiene needs, and electricity tariff strategies.
Customer handover
Essential explanations
DHW boost functions and recovery times.
Anti-Legionella cycle purpose and timing.
Impact on space heating during priority mode.
Notes: Tutor note:
Heat pump DHW usually requires higher temperatures than space heating. DHW priority must be set so the cylinder reheats reliably without causing avoidable comfort complaints.
Ask learners: what happens if DHW priority runs during the coldest part of the morning heating demand?

## Slide 18: Hot water priority
Key implementation requirements
Coordinate water heating with space heating demands to maintain comfort levels.
Select appropriate cylinder sizes to minimise recovery time and frequency of priority overrides.
Ensure control logic prevents prolonged loss of space heating in extremely cold weather.
Notes: Tutor note:
Heat pump DHW usually requires higher temperatures than space heating. DHW priority must be set so the cylinder reheats reliably without causing avoidable comfort complaints.
Ask learners: what happens if DHW priority runs during the coldest part of the morning heating demand?

## Slide 19
TRVs and zoning
Core concepts: Flow and control
TRVs restrict flow to individual radiators as rooms warm. Zoning manages groups of circuits independently for optimal comfort and efficiency.
System benefits
Zonal control
Useful for enhancing occupant comfort, managing unused rooms, and adapting to varying occupancy patterns.
Efficiency
Allows for targeted heating, reducing energy waste in unoccupied spaces.
Critical considerations
Flow limitations
Too many closed circuits can critically reduce flow rates and active water volume within the system.
Heat pump requirements
Heat pumps demand minimum flow/volume; zoning must be designed carefully to prevent operational issues.
Notes: Tutor depth:
TRVs are helpful but can be problematic if they shut down too much of the system. This can cause low flow, cycling or bypass issues. In heat pump systems, avoid uncontrolled conflict between TRVs, thermostats and weather compensation.
Stop point: learners identify when TRVs are useful and when they may create problems.

## Slide 20
TRVs and zoning
Commissioning checklist
Physical verification
Verify valve positions and operation.
Check flow rates and system balance.
Provide clear user instructions.
Design and implementation strategy
Ensure hydraulic separation or bypass arrangements to maintain heat pump flow when zones close.
Balance radiator outputs via TRVs to ensure even temperature distribution and system efficiency.
Train customers on the interaction between TRVs and the main thermostat to avoid conflicting settings.
Notes: Tutor depth:
TRVs are helpful but can be problematic if they shut down too much of the system. This can cause low flow, cycling or bypass issues. In heat pump systems, avoid uncontrolled conflict between TRVs, thermostats and weather compensation.
Stop point: learners identify when TRVs are useful and when they may create problems.

## Slide 21: Hybrid control systems
Coordinate the heat pump with another heat source
A hybrid system manages a heat pump alongside a secondary source (boiler/heater) to work together safely and efficiently.
Control strategy logic
Operational decisions
Based on outdoor temp, demand, cost, carbon impact, and tariffs.
Common strategies
Temp-based switchover
Cost and Carbon-based control
Demand-based backup.
Suitability and Risk
Property support
Ideal for high heat loss buildings or staged low-carbon transitions.
Logic requirements
Poor settings can cause short cycling or high emissions, reducing environmental benefits.
Professional standards
Competence boundaries
Gas Safe / OFTEC for combustion
Qualified electrical for backup
No working beyond competence.
Notes: Tutor note:
Hybrid systems are not just two appliances connected together. They need a control strategy. The switchover point may be based on outdoor temperature, tariff cost, capacity or customer needs.
Link to K1.8: Gas Safe/OFTEC competence applies to combustion appliances/fuel systems.

## Slide 22: Hybrid control systems
Commissioning and Handover
Record hybrid modes, switchover temps, and DHW priority strategies.
Explain when and why the backup source runs to the customer.
Identify and advise on settings the customer should avoid changing.
Notes: Tutor note:
Hybrid systems are not just two appliances connected together. They need a control strategy. The switchover point may be based on outdoor temperature, tariff cost, capacity or customer needs.
Link to K1.8: Gas Safe/OFTEC competence applies to combustion appliances/fuel systems.

## Slide 23
Apps and remote monitoring
Core functionality
Allows users or installers to view and control system settings remotely, offering real-time visibility into temperatures, schedules, energy use, and performance trends.
Operational benefits
Efficiency and Maintenance
Helps with early fault detection and reduces unnecessary physical call-outs through remote diagnostics.
Data insights
Provides access to performance trends and detailed energy usage data for optimised running.
Notes: Tutor depth:
Remote monitoring can identify trends such as repeated defrost, high flow temperatures, fault codes or loss of pressure. However, readings must be interpreted correctly and should be backed up by on-site checks when needed.
Prompt: what information would be useful to see before attending a fault visit?

## Slide 24
Apps and remote monitoring
Critical considerations
Technical infrastructure
Must ensure Wi-Fi reliability, robust data privacy measures, and clear support arrangements.
Safety boundaries
Remote monitoring is a tool for convenience and monitoring, not a replacement for scheduled servicing or on-site safety checks.
User guidance
Handover training
Ensure customer understands which settings are safe to adjust.
Clearly define the limitations of remote control.
Advise on data security and passwords.
Notes: Tutor depth:
Remote monitoring can identify trends such as repeated defrost, high flow temperatures, fault codes or loss of pressure. However, readings must be interpreted correctly and should be backed up by on-site checks when needed.
Prompt: what information would be useful to see before attending a fault visit?

## Slide 25
Time-of-use tariffs and smart scheduling
Market dynamics
Time-of-use (ToU) tariffs change electricity prices at different times, incentivising consumption when demand is low or renewable generation is high.
Scheduling logic
Smart controls
Controls may schedule Domestic Hot Water (DHW) or gentle pre-heating during lower-cost periods.
Operational balance
Must balance cost savings with comfort, hygiene, recovery time, and heat losses.
Integration and Efficiency
PV/Battery synergy
PV/battery integration can support daytime DHW or the use of stored energy during peaks.
Peak management
Avoid using immersion or backup heaters at peak tariff times unless strictly necessary.
Best practice
Documentation
Always record tariff-aware settings during commissioning.
Customer education
Explain the schedule and cost-saving logic clearly to the customer at handover.
Notes: Tutor note:
Tariffs can save cost but poor scheduling can reduce comfort or increase losses. Low-cost electricity is not automatically efficient if the system overheats the building or cylinder unnecessarily.
Scenario: customer has a cheap overnight tariff and a battery. What DHW schedule might be sensible? What risks need checking?

## Slide 26
Smart grids and demand response
Core concept: Flexible management
Smart grids use digital communication and data from smart meters to balance electricity demand and supply, crucial for low-carbon technologies like heat pumps.
Demand response
Shifting usage to when comfort and safety allow. Heat pumps can be adjusted during peak periods while protecting comfort and hot water needs.
Energy storage
Batteries store surplus PV or off-peak power. Thermal stores and building fabric act as storage to shift heating demand to lower-cost periods.
Grid Interaction
Surplus solar can be exported via tariffs. Controls decide between site use, storage, or export based on customer priorities.
Notes: Tutor depth:
Keep this awareness-level. Learners should know why heat pump controls may increasingly interact with electricity networks and flexible tariffs.
Tutor example
A home has an ASHP, solar PV and battery storage. During the day, the PV system may generate more electricity than the house is using. The control strategy could use some of this excess electricity to heat the hot water cylinder, charge the battery, or run the heat pump gently. If the battery is full and the cylinder is already satisfied, the remaining electricity may be exported to the grid under an export tariff.
At night, a time-of-use tariff may provide cheaper electricity. The system could charge the battery or schedule DHW heating during the low-cost period. However, if the system overheats the cylinder unnecessarily or uses the immersion heater too often, the running cost benefit may be reduced.
Learner takeaway
Smart grid control is about timing energy use intelligently. Low carbon systems can use, store or export electricity depending on tariffs, comfort needs, DHW demand and customer preference. The controls must be compatible, commissioned correctly and clearly explained to the customer.
Prompt: what loads are easier to shift — space heating, DHW, battery charging? Discuss limits: comfort, Legionella strategy, user needs.

## Slide 27
Smart grids and demand response
Implementation essentials
Consent and compatibility: Requires smart metering, communication links, and clear customer agreement.
Future-ready design: Integration must not compromise comfort, safety, or system longevity.
Installer responsibilities
Explain controls, limitations, and customer-adjustable settings.
Record smart-grid settings during commissioning and explain at handover.
Notes: Tutor depth:
Keep this awareness-level. Learners should know why heat pump controls may increasingly interact with electricity networks and flexible tariffs.
Tutor example
A home has an ASHP, solar PV and battery storage. During the day, the PV system may generate more electricity than the house is using. The control strategy could use some of this excess electricity to heat the hot water cylinder, charge the battery, or run the heat pump gently. If the battery is full and the cylinder is already satisfied, the remaining electricity may be exported to the grid under an export tariff.
At night, a time-of-use tariff may provide cheaper electricity. The system could charge the battery or schedule DHW heating during the low-cost period. However, if the system overheats the cylinder unnecessarily or uses the immersion heater too often, the running cost benefit may be reduced.
Learner takeaway
Smart grid control is about timing energy use intelligently. Low carbon systems can use, store or export electricity depending on tariffs, comfort needs, DHW demand and customer preference. The controls must be compatible, commissioned correctly and clearly explained to the customer.
Prompt: what loads are easier to shift — space heating, DHW, battery charging? Discuss limits: comfort, Legionella strategy, user needs.

## Slide 28
Compatibility and regulatory considerations
System compatibility
Controls must suit the heat pump, emitters, cylinder, and hydraulic layout. Boiler-style controls may hinder efficiency.
Communication
Verify methods: on/off, volt-free, bus (OpenTherm), or proprietary protocols. Incorrect types prevent modulation.
Conflict avoidance
Prevent conflicting commands (e.g. smart stats vs. weather comp or TRVs vs. min flow). Strategy must be coordinated.
Regulatory compliance
Must meet Building Regs and MCS for effective time/temp control and handover evidence.
Safety and Evidence
Controls must not disable safety functions. Record all settings for audit and warranty purposes.
Future readiness
Plan for integration with PV, storage, EV charging, and smart grid services.
Notes: Tutor note:
Compatibility is a common real-world problem. A generic smart thermostat may not access weather compensation or manufacturer features. Proprietary controls may be needed to achieve efficient operation.
Tutor example
A customer wants to fit a popular third-party smart thermostat to a heat pump. The thermostat can switch the system on and off, but it cannot communicate with the heat pump’s weather compensation or modulation controls. The heat pump then runs less efficiently, cycles more often, and loses some manufacturer control functions.
The correct approach is to check the heat pump manufacturer’s control compatibility list and confirm whether the third-party device can be used without disabling key heat pump features. If not, the manufacturer’s controller or an approved compatible control should be used.
Learner takeaway
Controls must be selected as part of the system design, not added as an afterthought. A compatible control strategy protects efficiency, comfort, safety, compliance, warranty and future serviceability.
Stop point: 'compatible or conflict?' scenario quiz.

## Slide 29
Compatibility and regulatory considerations
Key implementation requirements
Follow manufacturer wiring terminals and sensor requirements strictly.
All wiring and testing must be performed by competent persons following electrical regs.
Commissioning records must include schedules, setpoints, and weather curves.
Notes: Tutor note:
Compatibility is a common real-world problem. A generic smart thermostat may not access weather compensation or manufacturer features. Proprietary controls may be needed to achieve efficient operation.
Tutor example
A customer wants to fit a popular third-party smart thermostat to a heat pump. The thermostat can switch the system on and off, but it cannot communicate with the heat pump’s weather compensation or modulation controls. The heat pump then runs less efficiently, cycles more often, and loses some manufacturer control functions.
The correct approach is to check the heat pump manufacturer’s control compatibility list and confirm whether the third-party device can be used without disabling key heat pump features. If not, the manufacturer’s controller or an approved compatible control should be used.
Learner takeaway
Controls must be selected as part of the system design, not added as an afterthought. A compatible control strategy protects efficiency, comfort, safety, compliance, warranty and future serviceability.
Stop point: 'compatible or conflict?' scenario quiz.

## Slide 30: Control selection scenario: occupied family home
Scenario Overview
3-bed home, ASHP, radiators, cylinder. Family peak DHW use at 7am.
Comfort goal: warm living areas morning/evening, bedrooms cooler overnight.
Notes: Suggested learner answer:
- Weather compensation enabled with suitable curve.
- Modest overnight set-back rather than full off.
- DHW scheduled before peak use and anti-Legionella cycle explained.
- TRVs used for room comfort but key circuits kept open/minimum flow maintained.
- Customer shown schedules, boost and what not to change.
Workbook task created separately.

## Slide 31: Control selection scenario: occupied family home
Proposed Control Strategy (Justification Task)
Weather Compensation: Essential for maintaining high COP by varying flow temperature based on outdoor conditions.
Modest Set-back: Prevents the system from working too hard to recover from deep temperature drops in a high-thermal-mass building.
DHW Priority Schedule: DHW Priority Schedule: Fully charges the hot water cylinder before the morning peak demand period. During cylinder recovery, available heat-pump output may be prioritised to DHW, and space heating may temporarily pause or reduce. Scheduling DHW recovery in advance helps minimise disruption to space-heating comfort during occupancy.
Careful TRV Integration: Open zones/bypass maintained to ensure minimum flow rates required for the ASHP are never compromised.
App Monitoring: Proactive fault detection and remote support to maximise system uptime and customer satisfaction.
Output Task: Use the points above to justify your final selection in a professional handover document.
Notes: Suggested learner answer:
- Weather compensation enabled with suitable curve.
- Modest overnight set-back rather than full off.
- DHW scheduled before peak use and anti-Legionella cycle explained.
- TRVs used for room comfort but key circuits kept open/minimum flow maintained.
- Customer shown schedules, boost and what not to change.
Workbook task created separately.

## Slide 32: Activity: Match control type to situation
Scenario 1
Budget-conscious customer with simple routine
Scenario 2
Customer with PV/battery and time-of-use tariff
Scenario 3
Property with mixed UFH and radiators
Scenario 4
Hybrid heat pump + gas boiler system
Scenario 5
Customer needing remote fault support
Task Instructions
Match the most suitable control approach and explain one benefit and one risk for each choice.
Notes: Tutor guide:
Possible matches: simple programmable thermostat/controller; tariff-aware scheduling/app; zoning/mixed circuit control; hybrid controller; remote monitoring.
Stop point: group comparison; encourage learners to justify based on suitability factors, not personal preference.

## Slide 33: Recap checkpoint
1
Why is weather compensation useful for heat pumps?
2
What is the risk of deep setbacks?
3
How can TRVs cause problems if poorly applied?
4
What does hot water priority do?
5
Name one future-ready control feature.
Notes: Suggested answers:
1) Reduces flow temperature when possible, improving efficiency.
2) Slow recovery, high flow temperatures, comfort complaints.
3) Closed circuits can reduce flow/volume and cause cycling.
4) Temporarily gives cylinder/DHW demand priority over space heating.
5) App/remote monitoring, tariff scheduling, PV/battery integration, smart grid readiness.
Wordwall/Quizizz recap created separately.

## Slide 34: Summary + questions
Core coverage
K1.15 covers control types, operation, characteristics and suitability
The value of controls
Good controls support comfort, efficiency, compliance and user confidence
Heat pump strategy
Heat pumps usually benefit from steady, low-temperature control strategies
Selection criteria
Suitability depends on budget, compatibility, scalability and customer needs
Handover process
Handover must explain everyday controls and key settings
Notes: Final tutor prompt: ask learners to complete the sentence: 'A good heat pump control strategy…'.

## Slide 35
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.
Notes: Capture misconceptions and signpost where to find requirements (manuals, standards, site procedures).