## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.32: Design principles and their application to low carbon heating and hot water systems

## Slide 2: Introduction / starter
Warm-up
What makes one heating system design better than another?
Pair-share
List three reasons why a heat pump project may fail even when the heat pump itself is of good quality.
Notes: Stop point: 3–5 minute discussion. Draw out heat source, emitters, cylinder coil, pump, buffer/volumiser, expansion vessel, controls and water quality.

## Slide 3: Objectives (K1.32)
Explain key design principles for low carbon heating and hot water systems.
Apply buildability, integration of services, quality and cost to design decisions.
Explain embodied carbon, fabric-first design, adaptability and life-cycle thinking.
Assess ASHP noise, national and local planning requirements.
Describe MCS/Flexi-Orb installer standards and unit location restrictions.
Apply principles to real UK low-carbon heat projects.
Notes: Learners should understand suitability and integration, not just recognise product names.

## Slide 4: Design principles: overview 1
Buildability: Can the system be safely installed, commissioned, accessed, maintained and replaced within the available space?
Integration of services: Heating, plumbing, electrical, ventilation, controls and renewable technologies must operate as one coordinated system.
Quality and cost: The lowest initial price may create higher running, maintenance or replacement costs over the system’s life.
Notes: Tutor note: A low carbon system is not just a heat pump. It is a chain of components. If one link is wrong, the whole system can underperform.
Learner takeaway: Good low-carbon design balances performance, cost, carbon, practicality and long-term use—not simply the size or price of the equipment.

## Slide 5: Design principles: overview 2
Embodied carbon: Designers should consider the environmental impact of materials, refrigerants, manufacture, transport, replacement and disposal.
Fabric-first approach: Improve insulation, airtightness and heat retention before increasing plant capacity or selecting larger equipment.
Adaptability and life cycle: Systems should accommodate future changes, remain serviceable and support responsible repair, replacement and end-of-life disposal.
Notes: Tutor note: A low carbon system is not just a heat pump. It is a chain of components. If one link is wrong, the whole system can underperform.
Learner takeaway: Good low-carbon design balances performance, cost, carbon, practicality and long-term use—not simply the size or price of the equipment.

## Slide 6: Buildability
Can the selected design actually be delivered safely and economically?
Consider access, lifting, floor loading, pipe routes, cable routes and plant-room space.
Check outdoor-unit support, service clearances, condensate route and maintenance access.
Allow for installation sequencing and coordination with other trades.
Design for commissioning, future servicing and eventual replacement.
Avoid selecting equipment before access and installation constraints are understood.
Notes: Activity: learners rank the most important suitability factors for a small terrace, a rural property with land, and a flat with limited external space.
Tutor prompt
Would you still select the same cylinder if it cannot be carried through the property or replaced later?

## Slide 7: Buildability: domestic design scenario
A terraced house needs an ASHP, new cylinder and upgraded emitters
Side access is narrow; cylinder route includes stairs and tight doorways.
The outdoor wall is close to a bedroom window and the neighbour's boundary.
Existing pipe routes pass through finished rooms.
Discussion: In groups, identify five buildability constraints and one design change for each.
Notes: Tutor example: Poor ASHP siting can cause airflow recirculation, noise complaints and defrost water issues even if the unit is correctly sized.

## Slide 8: Integration of services 1
Low-carbon heating systems interact with several building services, so successful performance depends on coordinated design rather than isolated installation decisions.
Heating must integrate effectively with plumbing, electrical supplies, ventilation, domestic hot water, controls and other renewable technologies.
Solar PV, battery storage, EV charging and smart tariffs can influence electrical capacity, load management and control strategy.
Notes: Tutor note: GSHPs need correct ground loop design. Undersized collectors can cool the ground loop excessively and reduce performance. Highlight to students that a heat pump is one part of a building-services system, not an isolated appliance.
Learner takeaway: Low-carbon technologies perform best when every building service is designed to work as part of one complete system.

## Slide 9: Integration of services 2
Fabric upgrades that improve insulation and airtightness must be supported by an appropriate ventilation and moisture-control strategy.
Controls should coordinate the heat source, heating zones, pumps, valves and DHW priority without creating conflicting demands.
Poor coordination can result in delays, rework, higher costs, comfort problems and reduced system efficiency.
Notes: Tutor note: GSHPs need correct ground loop design. Undersized collectors can cool the ground loop excessively and reduce performance. Highlight to students that a heat pump is one part of a building-services system, not an isolated appliance.
Learner takeaway: Low-carbon technologies perform best when every building service is designed to work as part of one complete system.

## Slide 10: Quality and cost 1
Quality should be judged by system performance, including comfort, reliability, efficiency, compliance, ease of use and customer confidence.
Initial capital cost must be balanced against energy consumption, maintenance requirements, warranty support and expected service life.
Effective value engineering removes unnecessary cost without compromising safety, performance, accessibility or design intent.

## Slide 11: Quality and cost 2
Lower-cost equipment may lead to higher running costs, reduced reliability, limited technical support or more frequent service visits.
Inadequate commissioning, poor documentation and weak customer handover can reduce performance and undermine long-term value.
A whole-life cost assessment provides a more realistic measure of value than selecting the lowest installation price alone.
Discussion: Where might spending more at design stage reduce whole-life cost?
Notes: Learner takeaway: The best-value system is not necessarily the cheapest—it is the one that delivers reliable, efficient and compliant performance throughout its life.

## Slide 12: Embodied carbon 1
Embodied carbon is the greenhouse-gas impact created through raw-material extraction, manufacturing, transport, installation, maintenance, replacement and end-of-life disposal.
Low-carbon heating design should reduce operational carbon through efficient performance, while also considering the carbon already contained within the equipment and materials.
Copper, steel, aluminium, plastics, insulation, electronics, and refrigerants all contribute to the system’s whole-life environmental impact.
Retaining suitable pipework, emitters or controls can reduce waste and embodied carbon, provided safety, compatibility, and performance are not compromised.

## Slide 13: Embodied carbon 2
Unnecessary replacement, excessive pipework, oversized equipment and avoidable material use should be designed out wherever practical.
Refrigerant selection, leakage prevention, recovery and responsible disposal are particularly important because some refrigerants have a high global-warming impact.
Whole-life carbon assessment balances the carbon cost of installation against the operational savings achieved throughout the system’s service life.
Discussion: Should working radiators always be replaced, or only where evidence shows they are unsuitable?

## Slide 14: Fabric-first approach 1
Fabric first means reducing the building’s heat demand before selecting or increasing heating-system capacity. The aim is to improve the performance of the building envelope so less energy is required to maintain comfortable internal temperatures.
Improvements may include loft, wall and floor insulation, high-performance glazing, improved airtightness and treatment of thermal bridges around junctions, openings and structural elements.
A lower design heat loss can allow the use of a smaller heat pump, lower flow temperatures and more efficient emitter sizing, improving seasonal performance and reducing running costs.

## Slide 15: Fabric-first approach 2
Base any improvements on an accurate survey and heat-loss assessment. Choose cost-effective measures suited to the property’s age, construction and condition.
Coordinate airtightness with ventilation and moisture management to protect indoor air quality and prevent damp and mould.
Fabric-first retrofit improves comfort by reducing cold surfaces, draughts and temperature variation, while extending heat-pump run times and limiting supplementary heating.
Do not mask fabric weaknesses with a larger heat pump; this raises capital cost, electrical demand, cycling and operating costs.

## Slide 16: Fabric first: new build and retrofit
New-build projects offer the greatest design freedom: insulation levels, airtightness, thermal bridges, ventilation, heating distribution and low-temperature emitters can be coordinated from the outset.
Early integration can reduce design heat loss, allow for a smaller heat pump, and support lower flow temperatures, improving efficiency and occupant comfort.
Retrofit is generally more challenging because designers must work around existing construction, limited access, unknown defects, occupied rooms, existing services and customer budgets.
Retrofit surveys should identify the building’s age, construction, moisture condition, ventilation provision, thermal bridges and suitability for proposed fabric improvements.
Notes: Learner takeaway: A new build can be designed as one coordinated low-energy system; retrofit requires careful investigation, sequencing and risk management to improve the building without creating new defects.

## Slide 17: Fabric first: Publicly Available Specification
PAS 2035 supports a whole-dwelling approach, requiring proposed measures to be assessed as part of one coordinated retrofit strategy rather than installed in isolation.
PAS 2030 supports the quality installation, commissioning and handover of energy-efficiency measures, including the workmanship and process controls needed to achieve the intended design performance.

## Slide 18: Fabric first: Key considerations
Planned fabric upgrades must be confirmed and recorded before final heat-loss calculations and heat-pump selection; sizing against improvements that may never be completed could leave the dwelling underheated.
Increased airtightness must be matched by deliberate ventilation and moisture management – an efficient dwelling needs controlled fresh air, not uncontrolled draughts.
Poorly considered insulation can create condensation, damp, mould or interstitial moisture risks, particularly in older and traditionally constructed buildings.

## Slide 19: Adaptability
Adaptable design enables heating and hot-water systems to accommodate future changes without full replacement or major building disruption.
Plan for solar PV, batteries, EV charging, smart tariffs, demand response and home energy management.
Reserve electrical capacity, board space, cable routes, plant access and control interfaces for future upgrades.
Use compatible, configurable controls; avoid proprietary systems that restrict integration, monitoring, expansion or replacement.
Arrange pipework, isolation points and plant to simplify maintenance, component replacement and new connections. Allow for later connection to heat networks, communal systems or shared ground arrays.
Notes: Learner takeaway: A future-ready system meets today’s calculated demand while providing practical, maintainable routes for tomorrow’s technologies and changing customer needs.

## Slide 20: Future readiness
Future demand may change due to extensions, increased occupancy, additional bathrooms, home working, accessibility needs, or changes in hot-water use patterns.
Future readiness does not mean unnecessarily oversizing the heat pump or cylinder. Equipment should meet the current calculated demand while allowing sensible provision for known future changes.
Design records should clearly identify assumptions, spare capacity and future connection opportunities so that later designers and installers can understand the original design intent.

## Slide 21: Life cycle and maintenance
Life-cycle design covers a system from specification and installation to use, maintenance, replacement and disposal.
Place equipment so engineers can reach pumps, filters, valves, sensors, isolators and controls safely. Leave enough space for servicing, fault-finding and replacing major parts.
Plan checks, cleaning, pressure monitoring, control updates and drainage inspections. Position isolation valves and test points so parts can be serviced without shutting down the system.
At handover, explain maintenance schedules, warranties and the checks users must complete.
Notes: Tutor prompt: Students need to understand that maintainability must be built in from the start – accessible components, clear records, and planned servicing protect performance, reliability, and long-term value.

## Slide 22: Life cycle and reliability
Accurate design drawings, commissioning results, settings, certificates and service records provide a traceable history that supports troubleshooting, warranty claims and future system upgrades.
Designers should consider component availability, technical support and expected service life, as obsolete or inaccessible equipment can increase downtime and whole-life cost.
A system that cannot be maintained effectively is unlikely to remain safe, reliable or efficient throughout its intended operating life.
Notes: Tutor prompt: Students need to understand that maintainability must be built in from the start – accessible components, clear records, and planned servicing protect performance, reliability, and long-term value.

## Slide 23: End-of-life disposal
Plan end-of-life during design so equipment can be removed, repaired, reused or recycled.
Qualified staff must recover refrigerant using equipment and records; never release it into atmosphere.
Electrical parts may fall under WEEE rules and must use authorised recycling routes.
Recover valuable copper, steel, aluminium and plastics where practical.
Contain and dispose of glycol, oils, dirty water, filters and chemicals—never into drains or the environment.
Repair, refurbish or reuse serviceable parts when safety and performance are proven.
Notes: Learner takeaway: Responsible end-of-life design protects the environment, supports legal compliance and keeps valuable materials in use for as long as possible.

## Slide 24: Disposal and compliance
Designers should allow sufficient access, isolation points and removable connections so major components can be replaced without unnecessary damage to the building or surrounding services.
Product selection should consider expected service life, availability of spare parts, manufacturer support, recoverability of refrigerant and the recyclability of materials.
Waste-transfer documentation, refrigerant records and disposal certificates provide evidence that legal and environmental responsibilities have been met.
Notes: Learner takeaway: Responsible end-of-life design protects the environment, supports legal compliance and keeps valuable materials in use for as long as possible.

## Slide 25: ASHP noise emissions
Plan for noise early: it affects comfort, neighbours, planning and location.
Sound power (LwA) is the total noise; sound pressure (LpA) is the noise at one place.
Noise depends on distance, unit size, mode, nearby walls, barriers and other units.
Keep units away from bedrooms, neighbours’ windows, patios and quiet areas, especially overnight.
The Approved Document L (2026) advises avoiding sleeping areas and vibration-carrying surfaces. Choose quiet equipment and follow planning rules.
Use anti-vibration mounts, solid bases, flexible connections and supported pipes to stop vibration spreading through buildings.
Notes: Tutor note: Approved Document L (2026) - GOV.UK
Learner takeaway: Noise cannot be corrected reliably after installation—select a quiet unit, assess the location and control vibration at the design stage.

## Slide 26: Noise compliance and regulations
Approved Document E explains how buildings should reduce sound travelling through walls, floors and other parts. Check it when heat pumps, pipes or brackets could carry noise or vibration between rooms or neighbouring homes. It does not replace the outdoor ASHP noise check needed for planning.
Before choosing the final location, record the manufacturer’s noise data, the relevant MCS 020(a) calculation, the permitted development rules, and the local planning requirements. The rules differ across the UK, so always check the latest guidance for each project.
Notes: Tutor note: Resistance to sound: Approved Document E - GOV.UK

## Slide 27: ASHP noise assessment and mitigation
MCS 020(a) sets out a domestic ASHP sound calculation for permitted development in England.
Assessment considers the unit sound power, distance, barriers, reflections and sensitive receiver locations.
Poor siting can cause failure even when the heat pump is quiet on paper.
Mitigation may include relocation, anti-vibration supports, acoustic screening or different equipment selection.
Do not rely on guesswork: use current planning and scheme requirements. Record the assessment and customer/planning evidence.
Activity: Would you place an ASHP below a neighbour’s bedroom window if it gave the shortest pipe route?
Notes: Scenario: A small zoned system short-cycles when only one zone calls. Learners decide whether issue is minimum volume, flow, control logic or emitter sizing.

## Slide 28: National planning requirements
Design compliance: Designs must meet national planning and Building Regulations.
Permitted development: Rules vary by technology, property type and UK nation.
Planning permission: Heat pumps may require planning permission if certain conditions are not met.
Special designations: Listed buildings, conservation areas and protected landscapes may have extra restrictions.
Building Regulations: May cover electrical work, hot water safety, drainage and energy performance.
Pre-installation checks: Designers must check current laws and relevant scheme rules.
Important: Rules differ across England, Wales, Scotland and Northern Ireland.

## Slide 29: Local planning requirements
Policy and constraints: Local planning authorities may have additional policies, expectations or constraints.
Siting considerations: Check noise, visual impact, conservation areas, listed buildings and landlord requirements.
Environmental factors: Flood risk, coastal exposure, biodiversity and neighbour impact may affect design.
Retrofit programmes: Local authority retrofit or housing programmes may specify products, standards or approval routes.
Early engagement: Early engagement can reduce redesign, delays and customer disappointment.
Record keeping: Always record planning assumptions and advice received.
Notes: Tutor note: Chance for students to discuss “Why might two identical ASHP installations be acceptable in one location but not another?”

## Slide 30: MCS installer standards
MCS sets recognised certification standards for low-carbon technologies, products and installers.
MIS 3005-D covers heat-pump system design, installation, commissioning and handover.
Project files should evidence room-by-room heat loss, emitter suitability, equipment selection, hydraulic design and controls.
Commissioning results, settings, certificates, warranties and customer handover documents support quality assurance.
MCS 020(a) specifies the required sound assessment showing an ASHP meets permitted-development noise requirements in England.
Designers and installers must follow current MCS standards, relevant legislation and the manufacturer’s latest installation instructions.
Notes: Tutor notes: Remind students that quality assurance certification is about design evidence, not just installer branding.

## Slide 31: Flexi-Orb and certification schemes
Flexi-Orb is an independent certification and quality-assurance scheme for renewable and low-carbon technologies, including heat pumps.
Its heat-pump requirements cover survey, design, specification, installation, commissioning and customer handover.
Certification schemes demonstrate installer competence, consistent workmanship, traceable evidence and consumer protection.
Approval does not replace manufacturer instructions, Building Regulations, planning requirements or legal duties.
Designers must confirm the scheme accepted by the client, funder, grant programme or contract before work begins.
Design and commissioning records, certificates, warranties and handover prove compliance.
Notes: Learner takeaway: Certification provides a quality framework, but the designer and installer remain responsible for delivering a safe, compliant and correctly performing system.

## Slide 32: Unit location and proximity restrictions
External unit location must satisfy technical, planning and customer requirements:
Check manufacturer airflow clearances and avoid discharge-air recirculation.
Consider distance to neighbouring buildings, windows, doors, bedrooms and quiet areas.
Allow safe maintenance access and future replacement routes.
Manage condensate and defrost water so it cannot freeze on paths or entrances.
Assess visual impact, vibration transfer, flood risk and security.
Notes: Tutor note: Location choices directly impact system efficiency, acoustic compliance, safety, and neighbour relations.

## Slide 33: Design in practice: Enfield Council
Project: Shared ground loop heat pump retrofit for social housing.
Scale: Over 400 flats across eight tower blocks.
Design solution: Shared ambient ground arrays with individual in-dwelling heat pumps.
Buildability: Residents remained in occupation while works were completed.
Benefits: Reduced heating costs, improved control and major carbon savings.
Discussion: Why use shared ground loops instead of one central energy centre?
Notes: Suggested evidence: heat loss calculation, radiator outputs at design ΔT, cylinder coil rating/surface area, flow/return readings, pump settings, DHW recovery data, customer usage pattern.
Local Government Association – Enfield Council: Council Housing Heat Pumps https://www.local.gov.uk/case-studies/enfield-council-council-housing-heat-pumps
This provides the clearest independent overview. It confirms that the scheme served approximately 400 flats, used individual in-dwelling heat pumps connected to shared ambient ground-loop arrays, and avoided the need for a conventional central energy centre. The ground array comprised 100 boreholes drilled to depths of more than 200 metres.

## Slide 34: Design in practice: retrofit and local initiatives
Sutton dwellings: Heritage social housing retrofit using ground source heat pumps.
Design issues: dense urban site, historic fabric, boreholes, resident disruption and planning constraints.
Leeds RHINOS: Area-based shared ground arrays for heat pumps as a “new utility”.
Design issues: coordinated grid upgrades, private/social housing and neighbourhood regeneration.
Heat Pump Ready Programme: Government-backed innovation projects for scalable deployment.
Discussion: When is neighbourhood design better than one home at a time?
Notes: Sutton Dwellings — heritage social housing retrofit
Official project case study: Kensa – Central London social housing retrofit: Sutton Dwellings
The case study covers 81 Edwardian-era flats, 27 boreholes, individual ground-source heat pumps, restricted working space and coordination of drilling and other trades within a dense Central London site.
Video case study: Kensa – Decarbonising Sutton Dwellings with ground-source heat pumps
Suggested tutor-note wording:
Sutton Dwellings demonstrates how networked ground-source heat pumps can be incorporated into historic social housing in a dense urban location. Learners should consider heritage requirements, drilling access, integration of services, buildability, project coordination and the long-term value of shared ground infrastructure.
Leeds RHINOS — shared ground arrays as a “new utility”
Official GOV.UK project overview: Heat Pump Ready Stream 1 Phase 1 projects – Leeds RHINOS
Scroll to “Leeds, Yorkshire – Renewable Heat Infrastructure Network Operating System (RHINOS)”. The government overview explains the area-based approach, coordinated grid upgrades, deployment across private and social housing and neighbourhood regeneration.
Full official feasibility report: Leeds RHINOS – Heat Pump Ready Project Report PDF
The report examines shared borehole arrays serving clusters of homes, customer engagement, electrical-network capacity, fabric improvements, finance, quality assurance and the concept of ground infrastructure operating like a utility network.
Suggested tutor-note wording:
Leeds RHINOS explored shared ground arrays connecting individual heat pumps across groups of homes. The project considered whether ground infrastructure could operate as a new utility, similar to water, gas, electricity or broadband. Learners should consider grid coordination, street-level disruption, ownership, maintenance, customer engagement and equitable access across private and social housing.
Heat Pump Ready Programme
Official successful-projects directory: GOV.UK – Heat Pump Ready Programme: successful projects
This page provides links to the projects funded through Streams 1, 2 and 3, including high-density deployment, technology development, case studies, reports and programme videos.
Official programme background and aims: GOV.UK – Information about the Heat Pump Ready Programme
The programme was established to reduce heat-pump lifetime costs, improve the consumer experience, address electrical-network impacts and create evidence for future policy and large-scale deployment.
Suggested tutor-note discussion question:
When might neighbourhood-scale heat-pump design be more effective than installing systems one property at a time? Consider infrastructure costs, borehole access, electrical-network capacity, disruption, maintenance, consumer choice and opportunities to regenerate an entire neighbourhood.

## Slide 35: Design challenge: social housing estate
Scenario: Propose a low-carbon heating strategy, using K1.32 design principles, for a 1960s social housing estate with electric heating and poor EPC ratings.
Consider buildability, fabric, embodied carbon, cost, quality and resident disruption.
Assess ASHP noise, GSHP/shared ground loops, PV, plant space and local planning.
Identify certification scheme requirements and documentation evidence.
Groups present and justify their preferred design approach.
Notes: Suggested answers: coil area supports heat transfer at lower temperatures; volumiser adds volume while buffer may separate circuits; low flow reduces emitter output; ASHP airflow/noise, GSHP groundworks, WSHP permissions/water quality; controls coordinate demand, temps, pumps, valves and source selection.

## Slide 36: Knowledge check and summary
Focus on design judgement, not only technology selection.
Good designs are buildable, integrated, high-quality and cost-effective over their life.
Fabric-first and embodied-carbon thinking reduce demand and environmental impact.
ASHP siting, noise, planning and certification must be assessed before installation.
Real projects show that low-carbon heat can be delivered at the dwelling, estate and neighbourhood scale.
Complete the sentence: “A low-carbon system is well designed when…”
Notes: Final prompt: Ask learners to complete the sentence: “A low carbon system performs well when…”

## Slide 37
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.