## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint 1.33: Factors affecting the system design

## Slide 2
Introduction / starter
Warm up
A home is warm with a gas boiler at 70°C flow temperature. Why might it be cold after a heat pump is installed at 45°C?
Pair share
Identify one building or system factor that must be checked before selecting a heat pump.
Notes: Tutor Prompt
Low-carbon design is a whole-system exercise—not simply a heat-source replacement.

## Slide 3
Objectives
1
Explain how building fabric and insulation affect heating-system design.
2
Assess emitter suitability, flow temperature and heat distribution.
3
Consider domestic hot-water demand and appropriate control strategies.
4
Explain how hybrid and combined technologies can be integrated appropriately.
5
Apply design factors to a realistic retrofit scenario.

## Slide 4
The design challenge
Traditional gas boilers deliver high temperatures quickly, often masking weaknesses in building fabric, radiator sizing, or distribution.
In contrast, heat pumps are most efficient when producing lower flow temperatures over longer, steadier operating periods.
The core challenge
Can the building maintain the required level of comfort at a lower flow temperature, including during cold weather?
Design principle
A complete low-temperature system design
A heat pump should be designed as part of a complete low-temperature heating system – not fitted as a direct replacement for a high-temperature boiler..

## Slide 5
The design challenge
Whole-system considerations
1
Building fabric and insulation determine how much heat the property loses.
2
Heat emitters must provide enough output at the proposed lower flow temperature.
3
Pipework, pumps, and hydraulics must maintain correct flow rate and volume.
4
Domestic hot water provision must meet demand with a compatible cylinder.
5
Controls must support stable operation, weather compensation, and efficiency.

## Slide 6
Building fabric and heat loss
Heat loss is the starting point for low-carbon design. Buildings lose heat through walls, roofs, floors, windows, doors, and thermal bridges.
It also occurs via uncontrolled air leakage around gaps, service penetrations, and junctions.
Design principle
Start with the building and its heat loss.
Select the heat source and emitters only after the demand has been properly established.
The room-by-room calculation
An essential step for low-temperature heating.
It identifies demand in individual rooms (which whole-house averages can hide) to confirm whether radiators or underfloor-heating circuits can provide sufficient output.
Notes: Tutor note: Use a simple comparison: two identical heat pumps installed in different homes will not perform in the same way. A well-insulated property with low heat loss may maintain comfort at a lower flow temperature, while a poorly insulated property may need emitter upgrades, fabric improvements or a different design approach. Emphasise that a whole-house calculation alone can hide cold bedrooms, bathrooms, extensions or north-facing rooms; the design must identify the limiting room.
Learner takeaway:
Start with the building, not the heat pump. Accurate room-by-room heat loss determines whether the system can provide comfort efficiently at low flow temperature.

## Slide 7
Building fabric and heat loss
Key impacts of heat loss
Required heat-pump capacity
Size and type of heat emitters
Flow temperature needed to achieve comfort
Running costs and seasonal efficiency
Fabric improvements sequencing (before or alongside upgrades)
Real-property assumptions
Must reflect construction type, glazing, and insulation.
Avoid using existing boiler ratings, as they are often oversized.
Benefits of fabric upgrades
Loft, wall, or floor insulation reduces demand, enables lower flow temperatures, decreases emitter sizes, and boosts heat pump efficiency.
Notes: Tutor note: Use a simple comparison: two identical heat pumps installed in different homes will not perform in the same way. A well-insulated property with low heat loss may maintain comfort at a lower flow temperature, while a poorly insulated property may need emitter upgrades, fabric improvements or a different design approach. Emphasise that a whole-house calculation alone can hide cold bedrooms, bathrooms, extensions or north-facing rooms; the design must identify the limiting room.
Learner takeaway:
Start with the building, not the heat pump. Accurate room-by-room heat loss determines whether the system can provide comfort efficiently at low flow temperature.

## Slide 8
Insulation and airtightness
Insulation and airtightness are central to low-carbon heating design because they reduce the heat that the system must replace.
Loft, wall and floor insulation reduce transmission heat loss through the building fabric, while airtightness measures reduce uncontrolled infiltration through gaps around windows, doors, service penetrations, loft hatches, floors and junctions.
Improving the fabric can:
reduce the building’s design heat loss and required heat-pump capacity
allow lower flow temperatures while maintaining comfort
reduce the number or size of radiator upgrades required
improve temperature stability and reduce cold draughts
lower running costs and improve seasonal heat-pump efficiency.
Notes: Tutor note:
Use the contrast between a typical compliant new home and a Passivhaus-style home to show that “meeting Building Regulations” is not the same as achieving the lowest possible heat demand. Emphasise that airtightness is beneficial only when it is deliberate and paired with appropriate ventilation. Ask learners to identify three common leakage routes in a new build and three in a retrofit.
Learner takeaway:
Better insulation and controlled airtightness reduce heat loss, allowing lower flow temperatures, smaller emitters and more efficient heat-pump operation—but ventilation, moisture management and build quality must be designed alongside them.

## Slide 9
Insulation and airtightness
Sequencing matters
Where fabric improvements are planned, assess and incorporate them before final heat-pump, emitter and flow-temperature design.
Insulation should not be treated as an optional extra to make a low-temperature system practical.
Notes: Tutor note: Use the contrast between a typical compliant new home and a Passivhaus-style home to show that “meeting Building Regulations” is not the same as achieving the lowest possible heat demand. Emphasise that airtightness is beneficial only when it is deliberate and paired with appropriate ventilation. Ask learners to identify three common leakage routes in a new build and three in a retrofit.
Learner takeaway:
Better insulation and controlled airtightness reduce heat loss, allowing lower flow temperatures, smaller emitters and more efficient heat-pump operation—but ventilation, moisture management and build quality must be designed alongside them.

## Slide 10
Insulation and airtightness
Building Regulations and U-values
Part L sets minimum energy-efficiency requirements for new dwellings and for relevant renovation, extension and replacement work. A U-value measures how quickly heat passes through an element: the lower the value, the better insulation performance.
England limiting values for new-dwellings:
0.16 W/m²K for roofs
0.26 W/m²K for walls
0.18 W/m²K for floors
1.6 W/m²K for windows/doors
Compliance is assessed as a whole-building calculation. Local regulations should always be checked.
Passivhaus comparison
Passivhaus is a voluntary high-performance standard rather than a Building Regulations minimum.
It commonly aims for wall, roof and floor U-values in the region of 0.10–0.15 W/m²K, with high-performance windows typically around 0.8 W/m²K or better.
The exact target depends on building form, orientation, shading, thermal bridges and the full PHPP design model.
Notes: Tutor note: Use the contrast between a typical compliant new home and a Passivhaus-style home to show that “meeting Building Regulations” is not the same as achieving the lowest possible heat demand. Emphasise that airtightness is beneficial only when it is deliberate and paired with appropriate ventilation. Ask learners to identify three common leakage routes in a new build and three in a retrofit.
Learner takeaway:
Better insulation and controlled airtightness reduce heat loss, allowing lower flow temperatures, smaller emitters and more efficient heat-pump operation—but ventilation, moisture management and build quality must be designed alongside them.

## Slide 11
Insulation and airtightness
Airtightness: best performance, not just “less draughty”
Airtightness should be designed as a continuous, inspectable layer – not left to sealant at the end of the build.
A certified Passivhaus targets no more than 0.6 air changes per hour at 50 Pa (ACH@50Pa), verified by pressure testing. This requires planned detailing, careful workmanship and interim testing.
New build approach
Identify the airtightness line on drawings before construction
Use a continuous membrane, taped boards, or wet plaster layer
Seal junctions, service penetrations, ducts, and reveals
Carry out interim blower-door tests before finishes conceal defects
Coordinate airtightness with mechanical or background ventilation.
Notes: Tutor note: Use the contrast between a typical compliant new home and a Passivhaus-style home to show that “meeting Building Regulations” is not the same as achieving the lowest possible heat demand. Emphasise that airtightness is beneficial only when it is deliberate and paired with appropriate ventilation. Ask learners to identify three common leakage routes in a new build and three in a retrofit.
Learner takeaway:
Better insulation and controlled airtightness reduce heat loss, allowing lower flow temperatures, smaller emitters and more efficient heat-pump operation—but ventilation, moisture management and build quality must be designed alongside them.

## Slide 12
Insulation and airtightness
Retrofit approach
Prioritise obvious leakage paths: loft hatches, floors, pipes, chimneys
Improve insulation and airtightness together where possible
Avoid blocking intentional ventilation without alternatives
Consider moisture risk and fabric condition before insulating
Record completed measures and planned improvements.
Notes: Tutor note: Use the contrast between a typical compliant new home and a Passivhaus-style home to show that “meeting Building Regulations” is not the same as achieving the lowest possible heat demand. Emphasise that airtightness is beneficial only when it is deliberate and paired with appropriate ventilation. Ask learners to identify three common leakage routes in a new build and three in a retrofit.
Learner takeaway:
Better insulation and controlled airtightness reduce heat loss, allowing lower flow temperatures, smaller emitters and more efficient heat-pump operation—but ventilation, moisture management and build quality must be designed alongside them.

## Slide 13
Ventilation, moisture and occupant needs
Improving insulation and airtightness reduces heat loss, but it also reduces the amount of uncontrolled fresh air entering and leaving the property.
This means ventilation must be deliberately designed to maintain indoor air quality, remove moisture, and prevent condensation, mould growth, and fabric damage.
A low-carbon heating design must balance:
energy efficiency and reduced heat loss
thermal comfort in occupied rooms
fresh-air provision and indoor air quality
moisture control and protection of the building fabric
practical operation that the household can understand and maintain.
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 14
Ventilation, moisture and occupant needs
Moisture and damp: why ventilation matters
Everyday activities (cooking, showers, breathing) produce moisture.
If not removed, it condenses on cold surfaces, leading to mould and poor air quality. Insulation reduces risk, but poor detailing leaves thermal bridges.
Sealing without ventilation makes damp worse.
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 15
Ventilation, moisture and occupant needs
Whole-house ventilation approach
A strategy that considers how fresh air enters, moves, and leaves. It should not rely only on opening windows or occasional extractor fans. Depending on retrofit level, it may include:
background ventilation (correctly sized trickle vents)
intermittent extract (kitchens, bathrooms, WCs)
continuous mechanical (MEV) extracting from wet rooms
heat recovery (MVHR) supplying filtered fresh air
adequate air paths (door undercuts, transfer grilles).
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 16
Ventilation, moisture and occupant needs
Controls and practical operation
Controls should support steady, efficient heating. Large daily setbacks can slow recovery. The customer must understand:
how to use heating setpoints and schedules
why ventilation should not be routinely switched off
when filters need checking/replacing and how to reduce moisture
signs of condensation, mould, or persistent humidity.
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 17
Ventilation, moisture and occupant needs
Occupancy and room use
Heating and ventilation demand changes dynamically according to how the property is used:
families with frequent cooking/showers create more moisture
bedrooms need cooler temperatures but adequate overnight flow
bathrooms need higher temperatures and extraction
home offices need stable comfort conditions during the day
guest spaces shouldn't become persistently cold or damp
vulnerable people require stable, carefully managed heat.
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 18
Ventilation, moisture and occupant needs
The correct solution depends on:
property type
airtightness
existing routes
budget
retrofit scope
occupant needs.
Note: Systems must be commissioned, maintained, and explained. Blocked vents, switched-off fans, or dirty filters undermine performance.
Notes: Tutor note: Ask learners to compare two properties: a draughty home with no planned ventilation and a highly airtight retrofit with fans switched off. In both cases, the occupant may experience poor comfort or moisture problems, but for different reasons. Reinforce that airtightness and ventilation are not opposites: controlled ventilation is what allows a well-sealed building to perform safely and comfortably.
Learner takeaway:
A well-designed low-carbon home is warm, airtight where intended and properly ventilated. Controlling moisture through whole-house ventilation protects health, comfort and the building fabric while allowing the heating system to operate efficiently.

## Slide 19
Heat emitter suitability
Heat emitters must provide enough heat to meet the calculated design heat loss of each individual room at the proposed low-carbon system flow and return temperatures. This is particularly important when replacing a gas boiler with a heat pump, because many existing radiator systems were originally designed around much higher water temperatures.
Radiator output is not fixed. It reduces significantly as the mean water temperature falls. A radiator that provides adequate heat with a boiler operating at 70–80°C flow temperature may provide only a fraction of that output when the system is designed to operate at 35–50°C flow temperature.

## Slide 20
Heat emitter suitability
The designer must confirm, room by room:
the calculated heat loss for the room at design conditions
the existing emitter type, dimensions, location and condition
the emitter output at the proposed flow and return temperatures
whether furniture, radiator covers, curtains or poor positioning restrict heat release
whether the room has particular comfort needs, such as bathrooms, nurseries, home offices or highly glazed spaces.

## Slide 21
Heat emitter suitability
Existing radiators may be retained where their output is proven to be sufficient at the proposed lower temperature. Where there is a shortfall, possible solutions include:
fitting larger radiators to increase heat-emitting surface area
installing low-temperature radiators specifically designed for heat-pump systems
using fan-assisted radiators or fan convectors, which increase heat output at lower water temperatures but require electrical supply and consideration of noise/control
installing or extending underfloor heating, where suitable, because its large surface area can deliver useful output at low temperatures
improving insulation, airtightness and thermal-bridge performance to reduce the room heat loss
revising the overall hydraulic and control strategy where mixed emitter types are used.

## Slide 22
Heat emitter suitability
Mixed emitter systems
Many retrofit properties will use a combination of:
existing radiators
upgraded radiators
fan convectors
underfloor heating.
Mixed systems can work well, but they require careful consideration of differing temperature requirements.
flow rates and balancing;
zoning and control compatibility;
whether blending/mixing arrangements are needed;
minimum flow through the heat pump;
customer expectations around response time and noise.

## Slide 23
Heat emitter suitability
Low-temperature radiators
Low-temperature radiators are designed to provide higher output at lower flow temperatures than conventional panel radiators of similar wall area. They may achieve this through larger heat-exchange surfaces, deeper panels, additional convector fins or integrated low-energy fans.
They can be particularly useful where:
there is limited wall space for a much larger conventional radiator
a room has high heat loss but fabric improvement is limited
a retrofit requires improved output without major floor disruption
the system is designed around lower flow temperatures to protect heat-pump efficiency.
Important suitability note
However, “heat-pump radiator” is not a guarantee of suitability on its own. The selected model must still be checked against the manufacturer’s output data at the actual design flow, return and room temperatures.

## Slide 24
Flow temperature: Why it matters
Flow temperature is the temperature of the water leaving the heat pump and travelling to the radiators, underfloor-heating circuits or other heat emitters.
It is one of the most important design decisions in a low-carbon heating system because it directly affects heat-pump efficiency, emitter output, comfort and running cost.
How heat pumps work
A heat pump must “lift” heat from a lower-temperature source – such as outdoor air, ground or water – to the temperature needed by the heating system.
The greater the difference between the source temperature and the required flow temperature, the harder the compressor must work.

## Slide 25
Flow temperature: Why it matters
What flow temperature affects
This means:
lower flow temperatures generally improve efficiency and seasonal performance
higher flow temperatures increase compressor work, electricity consumption and wear associated with more demanding operation
a system designed for 35–45°c flow temperature will operate more efficiently than one requiring 55–60°c, if comfort is maintained
flow temperature must be selected alongside building heat loss, emitter outputs, pipework/hydraulics and comfort requirements.
Core design aim
The aim is not simply to choose the lowest possible temperature.
Select the lowest practical design flow temperature that can still meet the calculated heat loss of every room on the coldest design day.

## Slide 26
Flow temperature: Why it matters
Practical example
If most rooms are comfortable at 45°C but one north-facing bedroom is not, the correct response may be to improve that room’s insulation or upgrade its radiator.
Raising the flow temperature for the whole property may solve one room’s problem but reduce efficiency across the entire system.

## Slide 27
Flow temperature: Why it matters
Weather compensation
Adjusts the heat-pump flow temperature in response to outdoor conditions:
when mild outside, the building loses less heat, so the controller reduces flow temperature
when outdoor temperature falls, the controller gradually increases flow temperature
set through a weather-compensation curve, commissioned for the building, emitter system and occupants
a curve set too high wastes energy; a curve set too low leaves rooms underheated.
Steady-state operation
Weather compensation works best when the heating system is allowed to operate steadily.
Frequent thermostat boosts, deep setbacks, constant switching on/off, or closing too many TRVs can work against the control strategy and reduce performance.

## Slide 28
Flow temperature: Why it matters
Typical design considerations
These are design ranges, not automatic settings. Manufacturer performance data, the room-by-room heat-loss calculation and the selected emitter outputs must determine the final design temperatures.
Underfloor heating (UFH)
30–40°C typical flow temperature.
Large surface area is ideal for low-temperature heat pumps.
Consider circuit length, manifold design, floor finish, insulation, and surface temperature limits.
Low-temperature / oversized radiators
35–50°C typical flow temperature.
Larger panels, deeper radiators, convector fins or integrated fans increase low-temp output.
Always calculate output using actual proposed flow, return, and room temperatures.
Notes: Tutor note: Use a simple analogy: carrying a heavy box upstairs requires more effort than carrying it onto a low step. In the same way, a heat pump uses more electrical energy when it has to raise water from a cold outdoor source to a high flow temperature. Ask learners: “If one room is cold at 45°C flow temperature, should the whole system immediately be increased to 55°C?” Lead them towards checking the room heat loss, emitter output, insulation, balancing and control settings first.
Learner takeaway:
Flow temperature is an efficiency lever. Design the system to meet comfort at the lowest practical flow temperature, then use correctly commissioned weather compensation to adjust it as outdoor conditions change.

## Slide 29
Flow temperature: Why it matters
Fan convectors / assisted radiators
35–50°C typical flow temperature.
Provides higher heat output where wall space is limited.
Requires electrical supply, controls, and consideration of fan noise, maintenance, and preference.
Existing conventional radiators
Must be assessed individually; they may be suitable, oversized, or inadequate at low flow temperature.
Some may need to be enlarged, replaced, or supported by fabric improvements.
Avoid increasing whole system flow temperature until limiting room, radiator output, insulation, and balancing are checked.
Notes: Tutor note: Use a simple analogy: carrying a heavy box upstairs requires more effort than carrying it onto a low step. In the same way, a heat pump uses more electrical energy when it has to raise water from a cold outdoor source to a high flow temperature. Ask learners: “If one room is cold at 45°C flow temperature, should the whole system immediately be increased to 55°C?” Lead them towards checking the room heat loss, emitter output, insulation, balancing and control settings first.
Learner takeaway:
Flow temperature is an efficiency lever. Design the system to meet comfort at the lowest practical flow temperature, then use correctly commissioned weather compensation to adjust it as outdoor conditions change.

## Slide 30
Flow temperature: Why it matters
Domestic hot-water cylinder heating
Often requires a higher flow temperature than space heating.
Cylinder must have a heat-pump-compatible coil with sufficient surface area for efficient transfer.
Consider cylinder volume, household demand, recovery time, hygiene/pasteurisation strategy, and immersion backup.
Notes: Tutor note: Use a simple analogy: carrying a heavy box upstairs requires more effort than carrying it onto a low step. In the same way, a heat pump uses more electrical energy when it has to raise water from a cold outdoor source to a high flow temperature. Ask learners: “If one room is cold at 45°C flow temperature, should the whole system immediately be increased to 55°C?” Lead them towards checking the room heat loss, emitter output, insulation, balancing and control settings first.
Learner takeaway:
Flow temperature is an efficiency lever. Design the system to meet comfort at the lowest practical flow temperature, then use correctly commissioned weather compensation to adjust it as outdoor conditions change.

## Slide 31
Emitter options for retrofit
Retrofit projects rarely have a single “standard” emitter solution. The most suitable option depends on the room-by-room heat-loss calculation, available space, building fabric, proposed flow temperature, disruption acceptable to the customer and the existing heating distribution system.
The aim is to provide sufficient heat output at the lowest practical flow temperature, rather than increasing the temperature of the entire system to compensate for one weak room.
Oversized or upgraded radiators
Increasing radiator surface area allows more heat to be emitted at lower flow temperatures.
Options include longer radiators, double/triple-panel radiators, deeper convector models or additional radiators where layout allows.
This is often one of the least disruptive retrofit measures and can allow existing pipework to be retained where it is suitable.
Output must be checked using manufacturer data at the proposed low-temperature design condition—not the traditional boiler rating.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 32
Emitter options for retrofit
Low-temperature radiators
Purpose-designed low-temperature radiators can provide improved output where wall space is limited.
They may use larger convector surfaces or integrated low-energy fans to increase heat transfer.
They are particularly useful in high-heat-loss rooms where a conventional radiator cannot be enlarged sufficiently.
Electrical supply, controls, fan noise, cleaning and maintenance requirements must be considered where fans are incorporated.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 33
Emitter options for retrofit
Underfloor heating (UFH)
UFH has a large heat-emitting surface area and is generally well suited to low-temperature heat-pump operation.
It can provide stable, even comfort and can reduce the need for wall-mounted radiators.
In retrofit, installation may involve significant disruption because floor finishes, floor height, insulation, door thresholds, manifolds and pipe routes must all be considered.
Low-profile retrofit systems may reduce disruption, but their output and suitability must still be calculated.
Floor coverings can significantly affect performance; thick carpets, underlay and some timber finishes may limit heat output.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 34
Emitter options for retrofit
Mixed emitter systems
Many retrofit properties will use a combination of retained radiators, upgraded radiators, fan convectors and UFH.
Mixed systems can work effectively, but the hydraulic layout, flow rates, balancing and controls must be designed carefully.
Different emitter types may respond at different speeds, so zoning and room controls must avoid conflict.
Where different flow temperatures are required, the design may need separate circuits, blending arrangements or a revised emitter strategy.
The heat pump must still have adequate minimum flow and water volume during all operating conditions.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 35
Emitter options for retrofit
Fan convectors
Use a heat exchanger and fan to move air across the emitter, allowing useful output at lower water temperatures.
A practical solution for rooms with limited wall space, conservatories, extensions or rooms with high glazing.
Require an electrical supply and suitable controls, and customers should understand possible fan noise and the need to keep air paths clear.
Selected using manufacturer output data at the actual proposed flow and return temperatures.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 36
Emitter options for retrofit
Avoid designing around the weakest room
A single undersized radiator, poorly insulated extension or north-facing bedroom can become the limiting factor in a low-temperature design.
Raising the flow temperature for the whole property may improve that room but can reduce efficiency and increase running costs everywhere else.
First investigate targeted options: improve insulation, reduce draughts, increase emitter area, fit a low-temperature radiator or use a fan convector.
Only increase the overall design flow temperature where the evidence shows that this is the most appropriate whole-system solution.
Notes: Tutor note: Give learners a simple retrofit example: a property has eight radiators that are adequate at 45°C flow temperature, but one extension requires 1.5 kW and its existing radiator can only provide 700 W. Ask them to compare the likely consequences of raising the entire system to 55°C versus upgrading the emitter or improving the extension fabric.
Learner takeaway:
In retrofit, target the limiting room first. Increasing emitter output or reducing heat loss in one problem area is often more efficient than raising the flow temperature for the entire home.

## Slide 37
Heat distribution and hydraulics: Part 1
Hydraulic balance and design
Heat distribution and hydraulic design determine whether the system can deliver the heat produced effectively to emitters. The system must provide the correct balance between:
sufficient flow through the heat pump and emitters
acceptable pressure loss through pipework and components
low noise, vibration and pump energy use
stable operation during zoning, DHW heating and defrost cycles
access for commissioning, cleaning, servicing and future fault-finding.

## Slide 38
Heat distribution and hydraulics: Part 1
Stable heat-pump flow
A minimum flow rate protects the heat exchanger. The hydraulic arrangement must ensure this flow is available during all operating conditions, including when:
• TRVs or motorised valves close
space heating and DHW priority changes
the system enters/exits defrost
circulation pump speed changes
smart controls reduce demand.
Minimum-flow route: Achieved through an open circuit, correctly controlled bypass, buffer vessel, volumiser or another approved hydraulic arrangement.

## Slide 39
Heat distribution and hydraulics: Part 1
Pipework and Flow rate
Pipework must be sized to carry the required water flow rate without excessive resistance, noise or velocity. Heat pumps require higher flow rates than traditional boilers.
Existing pipework should be assessed for:
Pipe diameter, material, condition, route length; small-bore sections; long runs, bends, restrictive fittings; corrosion, sludge, or debris; insulation quality; and target flow rate feasibility.
Risk: Poor flow leads to high temperature differences, cold emitters, poor DHW recovery, flow alarms, high-pressure trips, short cycling and reduced efficiency.

## Slide 40
Heat distribution and hydraulics: Part 1
Pumps, valves and hydraulic components
Circulation pumps: Must deliver flow against calculated resistance. Oversized pumps cause noise/erosion; undersized cause cold rooms.
Motorised and zone valves: Positioned to protect the minimum flow route.
Bypass valves: Protect flow, but incorrect settings short-circuit heat.
Buffer vessels and Volumisers: Add volume, separation, or defrost support.
Low-loss headers and Plate heat exchangers: Must be technically justified.

## Slide 41
Heat distribution and hydraulics: Part 2
Flushing, filtration and water quality
Water quality is particularly important in low-temperature systems because reduced flow, blocked strainers or fouled heat exchangers can have a major effect on performance.
The design and installation should include:
effective flushing and cleaning before commissioning
suitable filtration, including magnetic filtration where appropriate
strainers positioned so they can be inspected and cleaned
correct inhibitor concentration for the system materials
glycol or antifreeze protection where required by the design
accessible drain, fill and sampling points
records of treatment, cleaning, pressure and commissioning readings.
Water treatment, cleaning and ongoing maintenance should follow the system manufacturer’s requirements and relevant guidance such as BS 7593.
Notes: Tutor note: Explain that heat pumps generally move a larger volume of lower-temperature water than a boiler system. Use the analogy of delivering the same amount of heat using warm water rather than very hot water: more water must often move through the system. Ask learners what could happen if several TRVs close at once and there is no planned minimum-flow route.
Learner takeaway:
A heat pump does not only need the right output—it needs the right hydraulic conditions. Pipework, pumps, valves, water volume and water quality must work together to maintain stable flow, efficient heat delivery and reliable operation.

## Slide 42
Heat distribution and hydraulics: Part 2
Commissioning and evidence
Hydraulic design must be verified during commissioning, and not simply assumed from drawings.
Commissioning should confirm:
system pressure and expansion-vessel condition
flow rate and pump settings
flow and return temperatures
temperature difference across the heat pump and emitters
correct valve operation and zone sequence
bypass, buffer or volumiser operation where fitted
filter/strainer condition and water-treatment records
stable operation during heating, DHW production and defrost where applicable.
Notes: Tutor note: Explain that heat pumps generally move a larger volume of lower-temperature water than a boiler system. Use the analogy of delivering the same amount of heat using warm water rather than very hot water: more water must often move through the system. Ask learners what could happen if several TRVs close at once and there is no planned minimum-flow route.
Learner takeaway:
A heat pump does not only need the right output—it needs the right hydraulic conditions. Pipework, pumps, valves, water volume and water quality must work together to maintain stable flow, efficient heat delivery and reliable operation.

## Slide 43
Minimum flow and system volume
Overview and Requirements
Heat pumps need stable water flow through their heat exchanger to transfer heat safely and efficiently. Unlike traditional boilers, they are sensitive to low flow due to lower operating temperatures.
System design must meet both:
manufacturer's required minimum flow rate
required minimum system water volume.
Why minimum flow matters
Insufficient flow causes high temp differences, reduced emitter output, poor DHW recovery, low-flow alarms, high-pressure trips, noisy valves, and compressor short cycling.
Common causes of low flow
Closed TRVs, shut zone valves, blocked filters, incorrect pump settings, restrictive pipework, or system air.
Notes: Tutor note: Use the analogy of a small saucepan on a powerful hob: a small volume heats up very quickly and then needs the heat reduced or switched off. A larger pan of water changes temperature more steadily. In a heat-pump system, sufficient active water volume and stable circulation help the heat pump run for longer, more efficient cycles.
Ask learners: “What could happen if six TRVs close, two motorised valves shut and the heat pump is still trying to circulate water?”
Learner takeaway:
Minimum flow and active water volume are not optional details. They protect the heat pump from cycling and faults, maintain stable heat delivery and support efficient operation. Use the manufacturer’s hydraulic requirements, then design the emitters, zones and controls around them.

## Slide 44
Minimum flow and system volume
Why water volume matters
Water volume provides thermal stability. Low volume causes rapid temperature spikes and frequent cycling, reducing seasonal efficiency and increasing compressor wear.
Active system volume
The volume remaining available to the heat pump during normal operation, including when zones close or TRVs restrict flow.
TRVs, zoning and active volume
Zoning controls must respect hydraulic limits. If too many TRVs close, the heat pump loses its circulation path and active volume falls below safe manufacturer thresholds.
Recommended mitigations
Use a permanently open emitter circuit, controlled bypass, reference room control, or dedicated buffer arrangements.
Notes: Tutor note: Use the analogy of a small saucepan on a powerful hob: a small volume heats up very quickly and then needs the heat reduced or switched off. A larger pan of water changes temperature more steadily. In a heat-pump system, sufficient active water volume and stable circulation help the heat pump run for longer, more efficient cycles.
Ask learners: “What could happen if six TRVs close, two motorised valves shut and the heat pump is still trying to circulate water?”
Learner takeaway:
Minimum flow and active water volume are not optional details. They protect the heat pump from cycling and faults, maintain stable heat delivery and support efficient operation. Use the manufacturer’s hydraulic requirements, then design the emitters, zones and controls around them.

## Slide 45
Minimum flow and system volume
Buffers and Volumisers
Used to add system volume, support defrosting, or provide hydraulic separation. They should not be fitted automatically without design justification.
Volumisers: Add volume to reduce cycling.
Buffer vessels: Provide volume and hydraulic separation.
Design and Commissioning
The designer and installer must verify hydraulic operation under all conditions and record key benchmarks:
minimum flow rate and calculated active volume
circulation pump settings and bypass route
flow/return temperatures at part and full load
defrost, space heating, and DHW priority stability
Notes: Tutor note: Use the analogy of a small saucepan on a powerful hob: a small volume heats up very quickly and then needs the heat reduced or switched off. A larger pan of water changes temperature more steadily. In a heat-pump system, sufficient active water volume and stable circulation help the heat pump run for longer, more efficient cycles.
Ask learners: “What could happen if six TRVs close, two motorised valves shut and the heat pump is still trying to circulate water?”
Learner takeaway:
Minimum flow and active water volume are not optional details. They protect the heat pump from cycling and faults, maintain stable heat delivery and support efficient operation. Use the manufacturer’s hydraulic requirements, then design the emitters, zones and controls around them.

## Slide 46
Domestic hot water requirements
Overview and Household Demand
Domestic hot water (DHW) must be designed separately from space heating. A system may keep the house warm but still provide a poor customer experience if the cylinder is too small, recovery is too slow or the heat pump and cylinder are not properly matched.
DHW design should begin with the household’s actual demand, including:
number of occupants and likely future occupancy
number of bathrooms, showers and baths
simultaneous use (e.g. two showers running at the same time)
bath size and expected hot-water volume
typical times of use, such as morning shower demand
customer expectations for recovery time
holiday-let, multi-generational or high-demand use patterns.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 47
Domestic hot water requirements
Heat-pump DHW recovery
Heat pumps normally heat cylinders more slowly than high-output gas boilers because they operate at lower primary flow temperatures and typically have lower instantaneous output. This must be allowed for in the design.
A suitable design considers:
cylinder storage volume and usable hot-water capacity
heat-pump output and cylinder coil heat-transfer area
time available for recovery between periods of demand
whether DHW priority pauses space heating and its effect on comfort
the role of any immersion heater for hygiene cycles or exceptional demand.
The aim is to store and recover water efficiently, rather than relying on frequent immersion-heater boosts.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 48
Domestic hot water requirements
Cylinder volume and coil area
A heat-pump-compatible cylinder commonly requires a larger heat-exchanger coil surface area than a conventional boiler cylinder. This is because the temperature difference is lower, so a larger coil is needed to transfer heat effectively.
Unchecked conventional cylinders may result in:
slow cylinder recovery and high heat-pump flow temperatures
poor heat-pump efficiency
frequent immersion-heater use
customer complaints about insufficient hot water.
The selected cylinder must be confirmed as compatible using manufacturer performance data.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 49
Domestic hot water requirements
DHW temperature, hygiene and safety
DHW design must balance energy efficiency, hygiene and scald prevention.
Stored hot water is commonly maintained at a temperature supporting Legionella control, determined by design and guidance.
Scheduled high-temperature cycles or immersion heaters may be used to achieve periodic pasteurisation where required.
Avoid unnecessary daily high-temperature operation to preserve efficiency.
Thermostatic mixing valves may be used at outlets to reduce scald risk, particularly in bathrooms or care settings.
Cylinder thermostats, sensor locations, and safety controls must be commissioned and recorded.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 50
Domestic hot water requirements
DHW priority and control strategy
DHW priority means the heat pump temporarily directs output to the cylinder rather than space heating. This improves recovery, but the design must consider:
how long space heating will be paused
whether the property has thermal stability to tolerate the pause
the likely demand pattern, tariff periods, and solar-PV generation
customer understanding of boost, holiday, and hygiene-cycle functions.
A well-insulated home may tolerate a pause with little effect. A poorly insulated home requires careful planning.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 51
Domestic hot water requirements
Design and Commissioning checks
The designer and installer should confirm and record:
household DHW demand and peak-use profile
cylinder volume, heat-pump compatibility, and coil surface area
heat-pump output at DHW temperatures
cylinder thermostat and sensor settings
DHW priority sequence and recovery time
immersion-heater purpose and control settings
pasteurisation/hygiene strategy
expansion, discharge, and unvented-cylinder safety arrangements
scald-protection measures and customer handover information.
Notes: Tutor note: Ask learners to compare two homes: a two-person property with one shower and a five-person household with two showers and a large bath. Both may have the same heat pump, but their cylinder size, coil requirements, recovery expectations and control strategy could be very different. Reinforce that “300 litres” alone does not prove a cylinder is suitable—the coil and heat-pump performance matter just as much.
Learner takeaway:
Good DHW design is about demand, storage, heat transfer and control. A heat-pump cylinder must be sized and matched so the household receives enough hot water without relying on inefficient immersion boosts or unnecessarily high flow temperatures.

## Slide 52
DHW priority and electrical backup
DHW priority overview
Domestic hot-water priority is a control strategy that temporarily directs the heat pump’s available output to the hot-water cylinder when DHW heating is required. During this period, space heating may pause or reduce, allowing the cylinder to recover more quickly.
Why it is important
A heat pump normally has lower DHW recovery output than a high-output gas boiler. Trying to meet both demands simultaneously can cause slow recovery and high operating temperatures.
Notes: Tutor note: Use a simple scenario: a household takes several showers between 7:00 and 8:00am on a cold morning. Ask learners whether it is better for the system to try to heat the house and cylinder at the same time, or to prioritise the cylinder for a planned period. Then ask what design evidence would show whether the household will still remain comfortable during that pause.
Learner takeaway:
DHW priority helps a heat pump recover hot water efficiently, but it must be designed around the property’s thermal stability and household demand. Immersion heaters are useful for defined backup, hygiene or exceptional demand—not as a permanent solution to poor cylinder design.

## Slide 53
DHW priority and electrical backup
How DHW priority works
The control system manages hot water in a clear, automated sequence:
controller detects cylinder temp is below target
motorised valve directs output to cylinder coil
space-heating circuits pause or reduce
once target is reached, space heating resumes
managed without routine customer intervention.
Notes: Tutor note: Use a simple scenario: a household takes several showers between 7:00 and 8:00am on a cold morning. Ask learners whether it is better for the system to try to heat the house and cylinder at the same time, or to prioritise the cylinder for a planned period. Then ask what design evidence would show whether the household will still remain comfortable during that pause.
Learner takeaway:
DHW priority helps a heat pump recover hot water efficiently, but it must be designed around the property’s thermal stability and household demand. Immersion heaters are useful for defined backup, hygiene or exceptional demand—not as a permanent solution to poor cylinder design.

## Slide 54
DHW priority and electrical backup
Impact on space heating
Consider if the household will notice temporary heating reductions:
well-insulated: minimal noticeable impact
poorly insulated: room temps can fall in cold weather
high demand / small coils: increases recovery time
control scheduling: Program around peak usage.
Immersion heaters and backup
Appropriate uses:
Hygiene cycles, maintenance resilience, exceptional guest demand, or off-peak solar/tariff usage.
Should NOT be used to mask:
Undersized cylinders, small coil areas, poor compatibility, or incorrect settings. Frequent use dramatically increases running costs.
Notes: Tutor note: Use a simple scenario: a household takes several showers between 7:00 and 8:00am on a cold morning. Ask learners whether it is better for the system to try to heat the house and cylinder at the same time, or to prioritise the cylinder for a planned period. Then ask what design evidence would show whether the household will still remain comfortable during that pause.
Learner takeaway:
DHW priority helps a heat pump recover hot water efficiently, but it must be designed around the property’s thermal stability and household demand. Immersion heaters are useful for defined backup, hygiene or exceptional demand—not as a permanent solution to poor cylinder design.

## Slide 55
DHW priority and electrical backup
Electrical capacity and smart ops
Where backup or smart controls are used, design must evaluate:
available supply capacity and circuit protection
combined loads (EV, cooking, heat pump)
smart-meter tariffs and time-of-use pricing
solar PV, storage, and grid-flexibility integration.
Handover and customer understanding
Show the customer the following parameters:
normal DHW schedule and recovery target temps
priority meaning and how boost/hygiene cycles run
how tariffs or solar PV influence the system
who to contact if recovery is unusually slow...
Notes: Tutor note: Use a simple scenario: a household takes several showers between 7:00 and 8:00am on a cold morning. Ask learners whether it is better for the system to try to heat the house and cylinder at the same time, or to prioritise the cylinder for a planned period. Then ask what design evidence would show whether the household will still remain comfortable during that pause.
Learner takeaway:
DHW priority helps a heat pump recover hot water efficiently, but it must be designed around the property’s thermal stability and household demand. Immersion heaters are useful for defined backup, hygiene or exceptional demand—not as a permanent solution to poor cylinder design.

## Slide 56
Control strategies
Overview and Coordination
Controls link system design and performance. A well-designed system can operate poorly if controls are incorrectly selected, badly commissioned or overridden by the user.
Aim: Steady, predictable operation at the lowest practical flow temp.
Controls should coordinate:
heat-pump operation and weather compensation
room temperature, occupancy, and emitter circuits
circulation pumps, zone valves, and minimum-flow
DHW heating, priority, and backup/hygiene cycles.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 57
Control strategies
Time schedules and set-backs
Heat pumps perform best with longer operating periods and modest temperature changes. Schedules must reflect building response time.
Set-back: Reduces target room temp instead of switching off. Highly suited to well-insulated homes or UFH.
Deep overnight setbacks: Create long morning recovery periods, forcing higher flow temps and lowering efficiency.
Underfloor heating (UFH): Retains slab heat, avoiding costly reheat cycles from a cold baseline.
Plan DHW schedules around tariffs, PV, and demand.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 58
Control strategies
Weather compensation
One of the most important controls. It adjusts the target heating flow temperature dynamically according to the outdoor temperature.
Mild outdoor: Controller reduces flow temperature.
Colder outdoor: Controller gradually increases flow.
Improves seasonal efficiency by operating at lower temps.
Set using a commissioned compensation curve:
curve too high – causes excess electricity use
curve too low – results in cold rooms during freezing weather.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 59
Control strategies
Zoning and stop-start avoidance
Zoning and local controls improve comfort but must not compromise hydraulic stability. Frequent on/off cycling reduces efficiency.
Excessive zoning: Closes too many circuits, reducing minimum flow. Requires bypass, buffer, or open circuit.
Conflicting commands: Avoid conflict between room thermostats, TRVs, and smart controls.
Compressor cycling: Stop-start operation degrades hardware. Avoid aggressive boosts that trigger backup heaters.
Preferred: Stable, low-temp weather-compensated flow.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 60
Control strategies
Load comp. and room influence
Some systems use internal room temperature information to make minor adjustments to heat-pump output or flow temperature.
Load compensation: Reduces flow temp when indoor temperature is close to or above target.
Room influence: Adjusts based on representative room. Useful to manage solar, cooking, or occupant gains.
Reference room: Avoid placement near direct sun, open fires, kitchens, drafts, or unusual heat sources.
Should support weather compensation, not replace it.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 61
Control strategies
Commissioning and handover
Installer should commission and record:
Weather compensation curve, design flow temp, room thermostat location, schedules, set-backs, DHW settings, zone valve sequence, and smart/PV integration.
Show the customer:
how to adjust room temperatures and schedules
why high-temperature overrides must be avoided
how DHW boost, holiday mode, and immersion run
how to use smart apps without hurting efficiency.
Notes: Tutor note: Ask learners to compare two control approaches. The first is a boiler-style approach: heating off overnight, 22°C boost every morning and TRVs shut in unused rooms. The second is a heat-pump approach: weather compensation, 19–20°C steady target, modest set-back and a planned DHW schedule. Ask which approach is more likely to maintain stable flow temperature and why.
Learner takeaway:
Good controls do not simply turn heating on and off. They coordinate the heat pump, emitters, DHW and user behaviour so the system can maintain comfort with steady, low-temperature, efficient operation.

## Slide 62
Zoning and TRVs
Zoning and TRVs overview
Zoning divides a heating system into separate areas that can be controlled independently, for example upstairs/downstairs, living areas/bedrooms, extensions or underfloor-heating circuits.
Thermostatic radiator valves (TRVs) provide local room control by reducing flow through an individual radiator as that room reaches its target temperature.
Used well, zoning and TRVs can improve comfort, reduce overheating in unused rooms and allow different parts of the property to follow different occupancy patterns. However, in a heat-pump system they must be designed carefully because every closed valve reduces the available water flow and active system volume.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 63
Zoning and TRVs
Required flow routes
A heat pump may require a reference room, open circuit or engineered minimum-flow route, depending on the manufacturer’s hydraulic requirements and the overall system design.
Reference room: representative living space where the main room thermostat/sensor is located. Radiator often left without TRV (or fully open).
Open circuit: remains available for water flow while the heat pump is operating (e.g. radiator or UFH).
Engineered route: bypass valve, buffer vessel, or volumiser to ensure flow even when TRVs close.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 64
Zoning and TRVs
Risks of poor strategy
If multiple TRVs or motorised zone valves close at the same time, the system may experience:
reduced or insufficient flow through the heat pump
high flow-to-return temperature difference
flow alarms, high-pressure trips or overheating protection
short cycling and reduced seasonal efficiency
noisy pumps, bypass valves or pipework
cold rooms when circuits reopen and system has to recover.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 65
Zoning and TRVs
Intelligent zoning design
Avoid treating every room as a separate aggressively controlled zone unless the hydraulic design supports it.
In many homes, a simpler strategy with:
weather compensation
sensible TRV settings
modest room-temperature adjustment
can provide better overall performance than multiple competing smart zones.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 66
Zoning and TRVs
TRV settings and guidance
TRVs should be used to fine-tune individual room temperatures, not to repeatedly switch the whole heating system on and off.
Keep the reference-room radiator fully open unless otherwise stated.
Avoid closing all radiators in a zone at the same time.
Set bedrooms, hallways, etc. slightly lower instead of fully closing.
Do not use TRVs to compensate for poor sizing or balancing.
Explain that heat pumps respond gradually; avoid frequent adjustments.
Check that furniture or curtains are not trapping heat around TRV heads.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 67
Zoning and TRVs
Commissioning and tecords
The installer should record:
the zoning layout and which areas are controlled independently
location of the reference thermostat or room sensor
intended TRV settings and open radiators/circuits
the minimum-flow strategy and manufacturer requirement
bypass, buffer or volumiser settings where fitted
valve sequence during space heating, DHW priority and defrost
customer handover info and any limitations on user adjustment.
Notes: Tutor note: Use a simple example: a home has eight radiators, each with a TRV, and three motorised zones. On a mild afternoon, most rooms reach temperature and all valves close. Ask learners: “Where will the heat-pump water circulate now?” Use this to introduce the need for a planned minimum-flow route rather than assuming the pump will always have somewhere to send water.
Learner takeaway:
Zoning and TRVs improve room comfort only when they are coordinated with the hydraulic design. Always protect the heat pump’s minimum flow, identify the reference room or open circuit, and explain the intended settings clearly to the customer.

## Slide 68
Hybrid systems: Purpose
Purpose and considerations
A hybrid heating system combines a heat pump with a second heat source (gas boiler, oil boiler, biomass appliance or electric resistance backup). Controlled as one system, it provides a practical transition route, but is not simply "a heat pump plus a boiler“ – it requires compatible hydraulics and coordinated controls.
Considered where:
peak heat demand is high and full electrification is difficult due to electrical supply or space
property has fabric limitations (solid walls, high heat loss) or space constraints
customer needs additional resilience or a staged retrofit is planned.
Aim for the heat pump to provide the greatest practical share of annual heat demand.
Notes: Tutor note: Present a rural, poorly insulated property with an existing oil boiler, limited electrical supply and small radiators. Ask learners whether hybrid is justified immediately, and what evidence they would need before deciding. Then ask how the answer might change after loft insulation, radiator upgrades and an electrical-supply upgrade.
Learner takeaway:
A hybrid system can be a useful transition solution, but only when it is justified by evidence and controlled properly. The heat pump should deliver the largest practical share of annual heat, while the secondary heat source supports genuine peak, resilience or staged-retrofit needs.

## Slide 69
Hybrid systems: Purpose
Hybrid design requirements
A hybrid design must assess:
room-by-room heat loss and demand
fabric improvements and insulation
emitter output at proposed flow temp
hydraulics, flow rates, and volume
cylinder and DHW strategy
existing boiler condition and efficiency
electrical supply and future needs
outdoor-unit location and constraints.
Competence: Work across refrigerant, gas, oil, biomass, and electrical systems must only be completed by registered, certified, and competent persons.
Notes: Tutor note: Present a rural, poorly insulated property with an existing oil boiler, limited electrical supply and small radiators. Ask learners whether hybrid is justified immediately, and what evidence they would need before deciding. Then ask how the answer might change after loft insulation, radiator upgrades and an electrical-supply upgrade.
Learner takeaway:
A hybrid system can be a useful transition solution, but only when it is justified by evidence and controlled properly. The heat pump should deliver the largest practical share of annual heat, while the secondary heat source supports genuine peak, resilience or staged-retrofit needs.

## Slide 70
Hybrid systems: Purpose
Typical hybrid operating approaches
Alternative bivalent operation: heat pump operates above a defined outdoor temp; boiler takes over below.
Parallel bivalent operation: heat pump operates first; backup assists when demand exceeds capacity.
DHW-focused backup: heat pump provides space heating and most DHW; backup supports peak demand.
Tariff- or carbon-led operation: controller selects heat source based on tariff, fuel cost, or grid carbon.
Control logic: The chosen approach must be supported by clear control logic. Poorly configured hybrids default to the boiler too often, reducing carbon savings and effectiveness.
Notes: Tutor note: Present a rural, poorly insulated property with an existing oil boiler, limited electrical supply and small radiators. Ask learners whether hybrid is justified immediately, and what evidence they would need before deciding. Then ask how the answer might change after loft insulation, radiator upgrades and an electrical-supply upgrade.
Learner takeaway:
A hybrid system can be a useful transition solution, but only when it is justified by evidence and controlled properly. The heat pump should deliver the largest practical share of annual heat, while the secondary heat source supports genuine peak, resilience or staged-retrofit needs.

## Slide 71
Hybrid systems: Purpose
Avoiding poor hybrid design
Hybrid systems must not be used to avoid basic design work.
It is not a substitute for:
calculating heat loss, improving insulation, or checking emitter suitability
designing pipework, minimum flow, and selecting compatible cylinders
commissioning weather compensation and explaining operation to the customer.
If the boiler is used for most heating due to undersizing, inadequate emitters, or poor controls, the system delivers limited carbon benefit and creates unnecessary cost and complexity.
Notes: Tutor note: Present a rural, poorly insulated property with an existing oil boiler, limited electrical supply and small radiators. Ask learners whether hybrid is justified immediately, and what evidence they would need before deciding. Then ask how the answer might change after loft insulation, radiator upgrades and an electrical-supply upgrade.
Learner takeaway:
A hybrid system can be a useful transition solution, but only when it is justified by evidence and controlled properly. The heat pump should deliver the largest practical share of annual heat, while the secondary heat source supports genuine peak, resilience or staged-retrofit needs.

## Slide 72
Hybrid system control logic
Overview and objectives
Hybrid controls decide which heat source operates, when it operates and whether both sources are allowed to run together.
The control strategy must be agreed at design stage and commissioned to reflect the property, heat pump, secondary heat source, tariffs and customer priorities.
The main objective:
allow the heat pump to provide the greatest practical proportion of annual heating and hot-water demand
while the secondary heat source supports genuine peak demand, resilience or specific operating conditions.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 73
Hybrid system control logic
Possible switchover inputs
The controller may use one or more inputs:
outdoor temp / heat load: outdoor threshold or demand vs. capacity limit
flow requirements: targets beyond efficient heat pump range
efficiency / cost / carbon: expected COP, electricity vs. fuel tariffs, or carbon intensity
DHW / fault: rapid recovery, hygiene cycles, or safe fallback.
Cost- or carbon-led controls must not override safety, minimum flow, hygiene, or manufacturer instructions.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 74
Hybrid system control logic
Alternative bivalent operation
Only one heat source operates at a time.
Heat pump provides heating while conditions permit.
At a defined bivalence point, the heat pump stops and backup takes over.
Bivalence point is based on outdoor temp, load, capacity, or flow requirements.
Simplifies hydraulics as sources do not run together.
If set too high, boiler runs too often and reduces savings.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 75
Hybrid system control logic
Domestic example: Rural house
Rural 3-bed house with oil boiler, upgraded radiators, and ASHP (45°C design).
Above 2°C outdoor temp: heat pump provides all space heating.
2°C to –2°C: parallel bivalent (boiler assists on high demand).
Below –2°C: alternative bivalent (heat pump stops, boiler runs).
ASHP heats DHW; immersion reserved for scheduled hygiene.
Settings reviewed after future planned fabric upgrades.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 76
Hybrid system control logic
Parallel bivalent operation
Heat pump and backup operate together when demand is high.
Heat pump normally operates first and provides lead heat.
Boiler/backup assists only when demand exceeds capacity.
Maintains comfort during cold spells without oversizing.
Hydraulic design must prevent unwanted mixing/short-circuiting.
Controls must clearly define priority and secondary enablement.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 77
Hybrid system control logic
Risks and competence boundaries
Poorly configured controls can cause:
Unnecessary boiler runs, short cycling, high flow temperatures, poor DHW recovery, increased costs, customer confusion, and warranty difficulties.
Installer handover details:
Must record bivalence point, weather compensation, DHW priority, and backup conditions.
Competence boundaries:
Work across refrigerant, gas, oil, electrical controls and unvented hot-water systems must be completed by certified and competent persons.
Notes: Tutor note: Ask learners to explain why the example should not automatically switch to oil at 5°C simply because the boiler can heat the house faster. This reinforces that hybrid controls should protect comfort and resilience while still allowing the heat pump to deliver the largest practical annual contribution.
Learner takeaway:
Hybrid controls must have a clear, evidence-based hierarchy. The heat pump should lead wherever practical, while the secondary heat source supports defined peak, resilience or exceptional conditions—not routine operation.

## Slide 78
Combining technologies
Low-carbon heating systems can be combined with other technologies to improve flexibility, reduce running costs and make better use of locally generated electricity.
The starting point remains: reduce heat demand through fabric improvement, size the heat pump correctly, then assess whether additional technologies provide a justified benefit.
Solar Photovoltaic (PV)
Generates electricity for the heat pump, battery, or household loads.
Smart controls can heat the DHW cylinder with surplus PV.
Highly dependent on roof orientation, shading, and season.
Solar Thermal
Uses sunlight to heat transfer fluid for domestic hot water.
Requires a compatible twin-coil cylinder or thermal store.
Requires careful coordination of solar and heat pump control settings.
Assess maintenance needs vs. PV plus heat-pump DHW.
Notes: Tutor note: Use a domestic example: a home has an ASHP, 250-litre heat-pump cylinder, 4 kWp solar PV and a smart tariff. Ask learners what should happen first on a sunny afternoon: heat the home unnecessarily, charge the cylinder within its safe operating range, charge the battery, or export electricity. The answer depends on the agreed control hierarchy, household demand and system state—not simply on “use all surplus PV”.
Learner takeaway:
Combined technologies can improve flexibility and reduce costs, but only when they are justified and coordinated. The heat pump, cylinder, PV, battery, solar thermal and smart controls must work to one clear operating strategy rather than competing with each other.

## Slide 79
Combining technologies
Battery storage
Retains PV electricity or charges during lower-cost tariff periods.
Supports evening demand but cannot assume full heat pump backup.
Requires electrical compatibility, ventilation, and fire safety checks.
Thermal storage
Stores heat in DHW cylinders, buffer vessels, or thermal stores.
DHW cylinder is the most straightforward domestic store.
Buffers should only be used where there is a defined hydraulic need.
Avoid oversized stores to minimise standing losses..
Notes: Tutor note: Use a domestic example: a home has an ASHP, 250-litre heat-pump cylinder, 4 kWp solar PV and a smart tariff. Ask learners what should happen first on a sunny afternoon: heat the home unnecessarily, charge the cylinder within its safe operating range, charge the battery, or export electricity. The answer depends on the agreed control hierarchy, household demand and system state—not simply on “use all surplus PV”.
Learner takeaway:
Combined technologies can improve flexibility and reduce costs, but only when they are justified and coordinated. The heat pump, cylinder, PV, battery, solar thermal and smart controls must work to one clear operating strategy rather than competing with each other.

## Slide 80
Combining technologies
Smart tariffs and flexible operation
Schedules operation during lower-cost periods based on time-of-use.
Requires proper building thermal mass and comfortable pre-heating.
Coordinating and appraising
Establish a clear control hierarchy to prevent systems from conflicting.
Prioritise safe DHW, then efficient heat pump operation.
Assess consumer-unit space, structural loads, and payback times before combining systems.
Notes: Tutor note: Use a domestic example: a home has an ASHP, 250-litre heat-pump cylinder, 4 kWp solar PV and a smart tariff. Ask learners what should happen first on a sunny afternoon: heat the home unnecessarily, charge the cylinder within its safe operating range, charge the battery, or export electricity. The answer depends on the agreed control hierarchy, household demand and system state—not simply on “use all surplus PV”.
Learner takeaway:
Combined technologies can improve flexibility and reduce costs, but only when they are justified and coordinated. The heat pump, cylinder, PV, battery, solar thermal and smart controls must work to one clear operating strategy rather than competing with each other.

## Slide 81
Design constraints and customer priorities
A successful low-carbon heating design must be technically sound, practical to install and suitable for the residents.
The designer should identify constraints early, before equipment is selected or quoted. This avoids late changes, unexpected costs, poor compromises, and customer dissatisfaction.
Space and access constraints
Systems require more space than simple boilers. Survey must confirm space for:
DHW cylinder, buffer vessel, volumiser, valves, and pipework
outdoor unit clearances, airflow paths, and maintenance access
cupboard size, door widths, floor loading, and lifting routes.
Electrical supply and infrastructure
Combined electrical loads (ASHP, EV, solar, battery) require careful evaluation:
incoming supply capacity, service fuse rating, and consumer-unit condition
dedicated circuits, earthing/bonding, and simultaneous peak loads
need for Distribution Network Operator (DNO) application/upgrade.
Notes: Tutor note: Give learners two customers with the same property. Customer A wants the lowest possible running cost and accepts radiator upgrades and a cylinder in a utility room. Customer B wants minimal disruption, no visible pipework and has limited cupboard space. Ask learners why the technically “best” heat-pump design may not be equally suitable for both customers.
Learner takeaway:
Good system design balances technical performance with real-world constraints and customer priorities. A solution is only suitable when it can be installed safely, operated effectively, maintained properly and accepted by the customer.

## Slide 82
Design constraints and customer priorities
Outdoor-unit location and siting
Siting must be assessed as part of the design, not after selection.
Consider:
airflow, recirculation, and distance from bedroom windows/boundaries
vibration transfer, noise assessment, and planning guidelines
defrost drainage to prevent ice on paths, steps, or neighbouring land.
Customer priorities and use
Discuss options instead of assuming.
Priorities vary across clients:
comfort vs. running cost, carbon reduction, and system fault resilience
minimal disruption, physical appearance, and noise levels
willingness to upgrade emitters now or adopt a staged transition.
Notes: Tutor note: Give learners two customers with the same property. Customer A wants the lowest possible running cost and accepts radiator upgrades and a cylinder in a utility room. Customer B wants minimal disruption, no visible pipework and has limited cupboard space. Ask learners why the technically “best” heat-pump design may not be equally suitable for both customers.
Learner takeaway:
Good system design balances technical performance with real-world constraints and customer priorities. A solution is only suitable when it can be installed safely, operated effectively, maintained properly and accepted by the customer.

## Slide 83
Design constraints and customer priorities
Planning and regulations
Identify permissions, building control, and landlord/lease constraints early:
outdoor unit size, location visual impact, and strict noise limits
conservation areas, listed buildings, and heritage constraints
structural amendments, consumer-unit upgrades, and cylinder safety.
Recording assumptions and scope
The design file protects the installer and customer by clearly documenting:
heat-loss calculations, emitter outputs, and fabric assumptions
equipment clearances, noise assessment, and electrical requirements
client compromises, scope exclusions, and other trades' duties.
Notes: Tutor note: Give learners two customers with the same property. Customer A wants the lowest possible running cost and accepts radiator upgrades and a cylinder in a utility room. Customer B wants minimal disruption, no visible pipework and has limited cupboard space. Ask learners why the technically “best” heat-pump design may not be equally suitable for both customers.
Learner takeaway:
Good system design balances technical performance with real-world constraints and customer priorities. A solution is only suitable when it can be installed safely, operated effectively, maintained properly and accepted by the customer.

## Slide 84
Scenario: 1930s retrofit
The Scenario
Property: three-bedroom semi, existing gas boiler, small radiators, partial loft insulation and one bathroom
01 Key Question: What information is needed before selecting a low-carbon heating solution?
02 Consider: Room heat loss, planned insulation, radiator outputs at lower temperature, pipework, cylinder space, DHW demand and electrical supply.
03 Discuss: Whether a heat-pump-only or hybrid option is justified – and what evidence would support the decision.

## Slide 85
Scenario: Design decision
Key principle
Resolve the limiting factors rather than raising flow temperature for the whole system
01 Evidence: Heat loss reduces after loft and cavity-wall work; most radiators are adequate at 45°C but two bedrooms are not.
02 Possible response: Upgrade the two emitters, retain compatible radiators, fit suitable cylinder and use weather compensation.
03 Check: Hydraulic flow, zoning arrangement, outdoor-unit siting, condensate drainage and customer controls.

## Slide 86
Common design mistakes
Design warnings
Avoid these critical errors when designing low-carbon systems
01 Sizing from the old boiler output rather than a heat-loss calculation.
02 Assuming all existing radiators will work at low temperature.
03 Selecting a standard cylinder with insufficient coil area.
04 Over-zoning or closing down system flow.
05 Using hybrid backup by default without clear control strategy.
06 Failing to record assumptions, calculations, manufacturer requirements and commissioning settings.

## Slide 87
Knowledge check
Review session
Confirm your understanding of low-carbon system design and limiting factors
01 Why does improving fabric often support lower flow temperatures?
02 What must be checked before retaining an existing radiator?
03 Why can a small cylinder coil be a problem with a heat pump?
04 Give one benefit and one risk of hybrid design.
05 How can poor zoning affect heat-pump operation?

## Slide 88
Summary
Core principle
Low-carbon system design begins with the building, not the heat pump
Interdependence
Fabric, heat loss, emitters, flow temperature, hydraulics, DHW and controls are interdependent.
Efficiency and comfort
Lower-temperature operation usually improves heat-pump efficiency, provided comfort can still be met.
Technology integration
Hybrid and combined technologies need clear justification and coordinated control.
Evidence-based decisions
Use calculations, manufacturer data and recorded design assumptions to support decisions.

## Slide 89
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.