## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.34: Planning, sizing and selecting practices for installations

## Slide 2
Introduction/starter
Scenario
A home has an old 24 kW gas boiler. Can an 8 kW heat pump be selected from the boiler rating alone?
Discussion: What evidence must be gathered before equipment is selected?

## Slide 3
Learning objectives
Plan installations by checking Distribution Network Operator (DNO) connection, building suitability, electrical supply, space, access, roof orientation and external siting.
Size heating, DHW and pipework using verified calculations.
Select equipment using calculated design requirements and manufacturer data.

## Slide 4
The design chain
01. Survey
Understand the building, its users and future plans.
02. Suitability
Check fabric, space, access, noise and electrical limits.
03. Room-by-room heat loss
Calculate how much heat each room needs.
04. Emitters and flow
Make sure radiators, pipes and pumps can deliver the heat.
05. Electrical supply and DNO
Check the supply and whether DNO approval is needed.
06. Hot water and solar
Size hot water and check whether solar or storage adds value.
07. Equipment selection
Choose equipment from the calculations—not the old boiler.
08. Commissioning plan
Plan what to test, record and explain to the customer.
Each step affects the next. Design the whole system, not just isolated parts.
Notes: Tutor notes:
Talk to students about the ‘one connected’ process. Each step affects the next. Design the whole system—not isolated parts. Ask learners to explain what could go wrong if the order is reversed—for example, selecting an outdoor unit first and only then checking room heat loss, electrical capacity and cylinder space.
Key risk: Skipping a step can lead to incorrect sizing, poor flow, or higher running costs.
Record the evidence: Surveys, calculations, choices, tests and handover.
Learner takeaway: A low-carbon system performs well only when the full design chain is followed. Survey first, calculate before selecting, and record the evidence that supports every decision.

## Slide 5
Planning: survey first
Survey before you size or quote. Record what is really there. The survey reveals heat demand, practical limits and possible upgrades—never size from the old boiler.
01. Building fabric
Check walls, roof, floors, insulation, windows and doors.
Record damp, draughts and any planned upgrades.
02. Ventilation and room use
Find fans, vents, chimneys and air leaks.
Note room use and any comfort or hot-water problems.
03. Existing heating/hot water
Check the boiler, radiators, controls and pipework.
Record cylinder details and signs of sludge or corrosion.
04. Space, routes and access
Measure space for equipment and future servicing.
Plan safe access plus pipe, cable and lifting routes.
05. Outdoor unit and drainage
Check airflow, noise, neighbours, weather and flood risk.
Plan safe access and drainage—avoid icy paths.
06. Spot constraints early
Check electrical capacity, DNO, planning and lease rules.
Resolve upgrades and access issues before quoting.
Notes: Tutor note: Ask learners why a survey should include questions about how the household uses hot water and which rooms feel cold, rather than only measuring walls and radiators. Reinforce that a technically correct system can still fail customer expectations if occupancy, comfort needs and practical constraints are ignored.
Learner takeaway:
Survey first, select later. Accurate survey information is the foundation for heat-loss calculations, equipment sizing, safe installation, realistic cost and a system that works for the household.

## Slide 6
Building suitability
Assess the whole home. A suitable design meets the home’s heating, hot-water, electrical and practical needs, not just the space for an outdoor unit.
01. Heat-pump suitability
Check heat loss, fabric, radiators, pipework and hot-water space.
Size from evidence, not the old boiler.
02. Solar PV suitability
Check roof direction, pitch, shading, condition and usable area.
Plan cabling, DNO limits and future EV or battery use.
03. Heat pump and PV
PV can support daytime loads and heat water when power is available.
Size the heat pump for cold winter demand, not sunny-day output.
04. Practical impact
Discuss space, noise, access, scaffolding and electrical upgrades.
Agree priorities: comfort, cost, carbon and appearance.
Notes: Tutor note: Ask learners to compare two homes with the same calculated heat loss. One has suitable radiators, a utility room for a cylinder, a clear outdoor-unit location and an unshaded south-west roof. The other has undersized emitters, limited plant space, difficult access and a heavily shaded roof. The heat pump may still be possible in both homes, but the design, cost, disruption and value of adding PV will be very different.
Learner takeaway:
Building suitability is whole-system suitability. A good design checks fabric, heat loss, emitters, hydraulics, DHW, space, access, electrical supply, outdoor siting and roof/PV potential before equipment is selected.

## Slide 7
Room-by-room heat loss part 1
01. Calculate each room
Use BS EN 12831-1 and MCS methods.
Base heat-pump size on calculated demand.
02. Add both heat losses
Fabric loss: heat through walls, roofs, floors, windows and doors.
Ventilation loss: heat carried away by moving air.
03. Gather the inputs
Measure room size, insulation, glazing and construction.
Set temperatures, air changes and room use.
04. Use the result
Choose emitter output, flow temperature and zoning.
One cold room can limit the whole system.
Calculate every room. Heat pumps must be sized from measured heat loss, not the old boiler or a whole-house guess.
Notes: Tutor note
Explain that installers should never estimate heat loss from floor area or the existing boiler size. A modern heat pump is selected using calculated building performance, not previous appliance ratings.
Learner takeaway
Every room is different. Accurate room-by-room heat-loss calculations provide the evidence needed to size the heat pump, select emitters and achieve efficient low-temperature operation.

## Slide 8
Room-by-room heat loss part 2
Worked example: Living room
1. Room volume and dimensions
Dimensions: 5.0 m × 4.0 m × 2.4 m Volume = 5 × 4 × 2.4 = 48 m³
2. External-wall heat loss
Area = 12 m² | U-value = 0.28 W/m²K Inside 21°C | Outside –3°C | ΔT = 24 K Q = U × A × ΔT = 0.28 × 12 × 24 = 81 W
3. Total room heat loss summary
Fabric = 610 W Ventilation (BS EN 12831) = 340 W Total = 950 W
Emitter selection requirement
Select an emitter rated at least 950 W at 45°C flow / 40°C return, using manufacturer data.
Real-world case study
Starting point
Three-bedroom detached; 30 kW gas boiler, over 20 years old.
BS EN 12831-1 / MCS MIS 3005-D assessment results: Total design heat loss = 8.4 kW Two bedrooms: larger radiators; lounge adequate. Loft insulation: 100 mm → 300 mm
After insulation
Revised design heat loss = 7.6 kW
Design choice
Select a 7.6 kW for local design outdoor temperature and 45°C flow—not oversized. This improves seasonal efficiency and lowers running costs.

## Slide 9
Electrical supply
Check the supply early. A heat pump adds a major electrical load, so assess it alongside EV charging, immersion heating, solar PV and batteries.
01. Incoming supply
Identify phase type, fuse rating and meter position.
The DNO owns the cut-out fuse; approval or an upgrade may be needed.
02. Phase and total load
Single-phase is common; three-phase supports larger combined loads.
Check compatibility, phase balance and DNO permission.
03. Consumer-unit safety
Check spare ways, protection, circuit size and isolation.
Confirm earthing and bonding with a qualified electrician.
04. Coordinate and record
Consider heat pump, EV, immersion, PV, battery and tariffs together.
Record circuits, equipment data, DNO approval and certificates.
Notes: Tutor note: Give learners a domestic example: a home has a 100 A single-phase supply, a 7 kW EV charger, electric shower, induction hob, 3 kW immersion heater and proposed heat pump. Ask them why they cannot simply add together appliance ratings and decide the supply is unsuitable. Then explain that they must still refer the assessment to a competent electrical designer/DNO process because maximum demand, diversity, protective devices and local network capacity all matter.
Learner takeaway:
Electrical planning is more than checking whether there is a spare way in the consumer unit. Confirm the supply type, main cut-out arrangement, maximum demand, protection, isolation, earthing, cable routes and DNO requirements before selecting and installing low-carbon equipment.

## Slide 10
DNO connection
Notify the DNO before work starts. Use “connect and notify” for compliant installs (notify within 28 days); otherwise apply and wait for approval.
01. Choose the route
Use the ENA EV/HP process or ENA Connect Direct.
The installer submits technical data; the customer gives consent.
02. Gather the details
Record address/MPAN, phase, fuse, meter and existing loads.
Add heat-pump data, backup loads, maximum demand and date.
03. Contact the DNO
Find the local DNO through ENA; suppliers handle meter or tariff issues.
PV and batteries use G98/G99, not the heat-pump route.
04. Engage early
Early contact can reveal upgrades, reinforcement or load management.
Never alter the DNO fuse, service cable or meter.
Notes: Tutor note: Give learners a scenario: a customer wants an ASHP, 3 kW immersion heater, 7 kW EV charger, PV and battery. Ask them to identify which parts are demand loads, which may export electricity, and why one generic “DNO form” is not enough without checking the current process.
Learner takeaway:
Confirm the DNO route before installation. Heat pumps use the ENA EV/HP process; PV and batteries use G98/G99. The installer must submit accurate technical information, follow either connect-and-notify or apply-to-connect requirements, and allow time for any network upgrade.

## Slide 11
Space and accessibility part 1
Plan space for installation and servicing. Equipment must be safe to lift, connect, maintain and replace, not just fit on the drawing.
01. Internal plant space
Allow room for the cylinder, vessels, valves, filters, pumps and controls.
Provide light, ventilation, drainage, frost protection and safe access.
02. Cylinder size and load
Heat-pump cylinders are large: 250 L holds about 250 kg of water; 300 L can exceed 350 kg full.
Check floor strength plus the lifting and replacement route.
03. Outdoor-unit support
Use a stable, level base with airflow, service access and vibration control.
Plan weather protection and drainage to prevent ice.
04. PV roof suitability
Check roof condition, rafters, wind/snow loads, cables and fire routes.
On flat roofs, protect the membrane, prevent ponding and avoid self-shading.

## Slide 12
Space and accessibility part 2
01. Ground-source heat pump (GSHP) space
Horizontal loops
Need large areas, suitable ground and machinery access. Check buried services, trees, foundations and drainage.
Boreholes
Use less land, but need drilling access, surveys, permissions and specialist design.
Plant-room space
Allow room for the heat pump, pumps, vessels, manifold, filters, buffer and controls.
02. Service access
Routine service points
Keep access to filters, fill and drain points, gauges, vessels, valves, pumps and PRVs.
Electrical and safety items
Keep isolators, controls, cylinder safety devices, solar and battery equipment, and outdoor-unit panels reachable.
Design for maintenance
Do not hide equipment behind fixed joinery or inaccessible ceilings. Allow simple servicing and replacement.
Notes: Tutor note: Ask learners to compare two proposed locations for a 250-litre cylinder: a ground-floor utility room with direct access, and a first-floor cupboard reached by a narrow staircase. Encourage them to consider not only whether the cylinder can be installed, but its full weight, floor loading, discharge route, maintenance access and eventual replacement.
Then ask: “A customer has a small garden but wants GSHP. What information is needed before deciding between horizontal loops and a borehole?”
Learner takeaway:
Space means more than footprint. Low-carbon equipment must be safely delivered, supported, connected, serviced and replaced. Check weight, structure, access, drainage, plant-room space and future maintenance before finalising the design.

## Slide 13
External siting part 1
Site the outdoor unit for clear airflow, low noise, safe drainage and easy servicing. Follow the manufacturer’s instructions and relevant rules.
01. Airflow and clearance
Keep the inlet and discharge clear, using the manufacturer’s minimum distances.
Avoid walls, fences, shrubs and layouts that recirculate cold air.
02. Noise and vibration
Keep the unit away from bedrooms, patios and neighbours where possible.
Check reflective walls and use suitable mounts to limit vibration.
03. Rules and permissions
Follow MCS MIS 3005-D, Building Regulations and planning rules.
Check listed-building, conservation-area and landlord restrictions.
04. Condensate drainage
Defrost water must drain freely and safely, even during freezing weather.
Prevent standing water and ice on paths; use a suitable drain or soakaway.

## Slide 14
External siting part 2
Protect the outdoor unit from weather and damage while keeping airflow clear, servicing safe, and pipe and cable routes short.
05. Environmental protection
Check flood, snow, salt, wind, debris, roof run-off, impact and vandalism risks.
In coastal or exposed areas, plan corrosion protection and maintenance.
06. Maintenance access
Leave room to remove panels, clean coils, test equipment and replace major parts.
Avoid sites needing scaffolding, fence removal or unsafe working positions.
07. Pipework and cables
Keep routes short and protected to reduce losses, bends and freezing.
Insulate and support pipes; add UV and impact protection where needed.
08. Choose the best location:
under a bedroom window;
open garden;
enclosed courtyard.
Choose B for airflow, short pipework, drainage, low noise and easy access.
Notes: Tutor note
Ask learners:
"Would you choose the shortest pipe run if it placed the heat pump beneath a bedroom window with poor airflow?"
Encourage discussion around balancing:
efficiency;
noise;
planning;
maintenance;
customer expectations;
manufacturer requirements.
Reinforce that external siting is a design decision—not simply an installation decision.
Learner takeaway
The best location for an outdoor unit is rarely just the nearest wall. External siting must satisfy manufacturer guidance, MCS requirements, Building Regulations, planning constraints and good engineering practice while ensuring unrestricted airflow, safe drainage, low noise, easy maintenance and long-term system performance.

## Slide 15
Roof orientation and solar part 1
Survey the roof before choosing solar. Check energy yield, structure, safety, usable area and long-term access.
01. Orientation and pitch
South gives the highest UK yield; east/west spreads output; north gives less.
Check pitch and elevations with design software.
02. Shading
Check buildings, chimneys, roof features and trees.
Change the layout or use optimisers; confirm the system still offers value.
03. Structure and area
Check roof condition, structure, fixings, loading and lifespan.
Leave space for edges, fire access, obstacles and maintenance.
04. Solar PV design
PV can run the heat pump, hot water and batteries, or export.
Plan demand, tariffs, inverter, cables, isolation and DNO rules.

## Slide 16
Roof orientation and solar part 2
Use solar to support the heat pump and hot water, but always size heating for the coldest design conditions.
05. Solar thermal
Check the cylinder coil, collector, pipes, pump, vessel and glycol.
Helps summer hot water, but contributes little to peak winter heating.
06. Heat-pump integration
PV can run the heat pump, heat water or charge a battery.
Do not subtract solar from heat loss; size to BS EN 12831-1 and MCS MIS 3005-D.
07. Maintenance and future
Plan safe access, cleaning and component replacement.
Allow for future shade, reroofing, expansion and EV charging.
08. Case study
35° south-west roof; no shade; 8 kW ASHP; 250 L cylinder; future EV.
Use 5 kWp PV, nearby inverter, battery and smart hot water; size the ASHP from heat loss.
Notes: Tutor note
Show learners two properties:
one with an unshaded south-facing roof;
one with a heavily shaded north-facing roof.
Ask:
Would both properties justify the same PV design?
Then ask:
Should either property's heat pump be made smaller because solar PV is being installed?
Use this to reinforce that solar technologies improve annual efficiency and reduce running costs, but they do not reduce the design heat load used for heat-pump sizing.
Learner takeaway
A good solar survey is about much more than roof direction. Assess orientation, pitch, shading, structure, usable area, cable routes, future maintenance and integration with the heat pump. Solar PV and solar thermal can significantly improve annual energy performance, but the heat pump must always be sized using the property's calculated design heat loss and verified manufacturer performance data.

## Slide 17
Space-heating requirements part 1
Combine room heat losses to size the heating system. Then check water volume, the hardest room to heat and the correct design temperatures.
01. Total heating requirement
Add all room losses to find the kW needed on the winter design day.
Use this to select the heat pump, emitters, pipes, pump and controls.
02. System water volume
Too little water causes cycling, alarms, wear, poor comfort and lower efficiency.
Check system volume and manufacturer limits; add a vessel only if justified.
03. The limiting room
The hardest room to heat may set the emitter size and flow temperature.
Improve its emitter or insulation. A larger heat pump alone will not fix it.
04. Design temperatures
Use local outdoor and agreed room temperatures, actual fabric and ventilation losses.
Record inputs; follow BS EN 12831-1 and MCS MIS 3005-D.

## Slide 18
Space-heating requirements part 2
01. Practical example: proposed system
Design heat loss
A detached home has a calculated total design heat loss of 8.2 kW.
Proposed system
12 radiators and 180 litres of system water.
Design flow temperature: 45°C.
Design temperature difference: ΔT 5 K.
02. Volume assessment and decision
Manufacturer requirement
The selected heat pump needs a minimum system water volume of 150 litres.
Design decision
The available 180 litres exceeds the minimum, so no additional buffer vessel is required. This supports efficient operation with lower pumping energy and less temperature mixing.
Alternative scenario
If the system held only 90 litres, review the hydraulic design and decide whether a volumiser or buffer vessel is needed, following the manufacturer’s guidance.
Notes: Tutor note
Explain that heat demand (kW) and system water volume (litres) are two different design considerations.
Heat loss determines how much heat the building needs.
Water volume determines how effectively the heat pump can deliver that heat.
A system can have the correct heat pump but still perform poorly if the hydraulic volume is insufficient.
Learner takeaway
The space-heating requirement is more than just the building's heat loss. Designers must calculate the total heating demand, confirm adequate system water volume, and ensure the hydraulic system, emitters and heat pump work together to provide efficient, reliable low-temperature heating.

## Slide 19
Heat-pump selection
Choose the heat pump from the calculated heat loss and real operating conditions, not the old boiler size or the model name.
01. Start with heat loss
Use the property’s calculated design heat loss in kW for the local winter design day.
Follow BS EN 12831-1 and MCS MIS 3005-D.
02. Check real performance
Check output at the local outdoor temperature and required flow temperature.
Use manufacturer data—not nominal model output.
03. Check the whole system
Review SCOP, electrical demand, operating limits, minimum flow and system water volume.
Also check hot water, cylinder recovery, controls and zoning.
04. Choose and record
Oversizing causes cycling, higher cost and lower efficiency; undersizing risks poor comfort.
Record heat loss, selected performance data and the final design decision.
Notes: Show learners two manufacturer performance tables for an 8 kW nominal heat pump. One delivers 8.0 kW at A7/W35, but only 6.7 kW at A-3/W45. Ask:
"Would this unit still be suitable for a property with a calculated design heat loss of 7.2 kW?"
This demonstrates why manufacturer performance at the actual design conditions is far more important than the model name or nominal output.
Learner takeaway
Heat pumps are selected using engineering evidence—not assumptions. Always choose the heat pump using the calculated design heat loss, local design temperatures, required flow temperature and verified manufacturer performance data to ensure efficient, reliable and compliant system operation.

## Slide 20
Oversizing and undersizing
A heat pump should match the building’s calculated heat loss at winter design conditions. Bigger is not automatically better.
01. If it is too small
It may not keep rooms warm in very cold weather and may rely on costly electric backup.
It can run flat-out, wear faster and take longer to heat water.
02. If it is too large
It may have a short cycle (starting and stopping often), which lowers SCOP and increases wear.
You also pay for unused capacity and may need more complex controls.
03. Aim for the right size
Match calculated heat loss and check output at the required outdoor and flow temperatures.
Use suitable emitters and manufacturer performance data.
04. Example: 7.8 kW loss
A 6 kW unit may need backup heat; a 12 kW unit may cycle and cost more.
Choose a unit that delivers about 7.8 kW at the actual design conditions.
Notes: Tutor note
Ask learners:
"If a customer asks for the 'next size up' to be safe, would you recommend it?"
Discuss why "bigger is better" is often true for traditional boilers but not for modern inverter-driven heat pumps. Reinforce that professional designers rely on calculated evidence, not assumptions or customer perception.
Learner takeaway
A correctly sized heat pump is neither oversized nor undersized. It should be selected using the calculated design heat loss, verified manufacturer performance data and recognised design standards to deliver efficient, reliable and comfortable low-carbon heating.

## Slide 21
DHW sizing
Size domestic hot water for the household’s real demand and the heat pump’s slower recovery—not simply for the biggest cylinder that fits.
01. Assess demand
Check occupants, bathrooms, showers, baths, simultaneous use and recovery time.
Allow for lifestyle and future changes.
02. Use a sizing guide
1–2 occupants: 120–180 L; 3–4: 180–250 L; 5+: 250–300+ L.
Confirm the final size from calculated demand.
03. Select cylinder and controls
Choose the correct volume, heat-pump coil, insulation and recovery.
Include DHW priority, pasteurisation, TMVs and PV controls.
04. Family-of-four example
Two bathrooms, two showers daily, occasional bath and 8 kW ASHP.
Select 210 L with compatible coil, DHW priority, weekly pasteurisation and PV diversion.
Notes: Tutor note
Ask learners:
"Would you choose a 300-litre cylinder for a couple living in a two-bedroom bungalow?"
Discuss why oversizing the cylinder can increase standing heat losses, take longer to recover and cost more, while undersizing may lead to frequent reheating, poor hot-water availability and customer dissatisfaction.
Reinforce that DHW sizing should always be based on calculated demand and manufacturer guidance, not on available space or assumptions.
Learner takeaway
A successful DHW design balances household demand, cylinder capacity, recovery time and heat-pump performance. Always size the cylinder from the customer's hot-water requirements and ensure it is specifically designed for use with a heat pump.
I actually think this is stronger than the qualification specification alone, because it gives learners real-world design guidance that reflects how installers and designers work with manufacturers such as Vaillant, Mitsubishi Electric, Daikin, NIBE and Viessmann, while still remaining aligned with MCS MIS 3005-D and industry best practice.

## Slide 22
Solar and hot-water requirements
Solar can reduce imported energy and support hot water, but it must not replace correct heat-loss or DHW sizing.
01. Coordinate the system
Prioritise comfort and safe DHW, then use solar and minimise grid electricity.
Check roof, structure, cylinder, controls and maintenance access.
02. Solar PV
Use daylight electricity for the heat pump, hot water or battery charging.
Check orientation, shade, roof area, structure, cables, inverter, EV and battery plans.
03. Solar thermal
Use a compatible twin-coil cylinder, collector, glycol circuit, vessel, pump and controller.
Plan stagnation protection and safe maintenance access.
04. Worked example
8 kW ASHP; 210 L cylinder; 4.5 kWp PV; 5 kWh battery; four occupants.
20 kWh solar − 8 kWh loads = 12 kWh for DHW, battery or export; winter heat loss is unchanged.
Notes: Tutor note
Ask learners:
A customer wants to reduce the size of their heat pump because they are installing a 6 kWp solar PV system. Would this be good design practice? Why?
Guide learners to explain that the design heat loss occurs during the coldest winter conditions, when solar generation is often at its lowest. Therefore, the heat pump must always be sized using the calculated building heat loss and verified manufacturer performance data, not expected solar generation.
Learner takeaway
Solar PV and solar thermal can significantly reduce annual energy consumption and improve system efficiency, but they do not replace correct heat-loss calculations. A successful design integrates solar technologies through compatible cylinders, intelligent controls and a clear operating strategy while ensuring the heat pump remains correctly sized for the property's design heating demand.

## Slide 23
Pipe sizing 1
01. Calculate the pipe size
Start with the system
Use the design heat output, required flow rate and flow/return temperature difference (ΔT).
Check the whole circuit
Use the actual internal diameter, total pipe length and every bend, tee, valve, filter, manifold and heat exchanger.
Confirm performance
Check water velocity, pressure loss, pump performance and manufacturer requirements.
02. Apply guidance and adjust
Use recognised guidance
Follow BS EN 12828, the CIBSE Domestic Heating Design Guide, manufacturer hydraulic guidance and MCS MIS 3005-D.
Allow for glycol
Glycol is more viscous than water, so resistance increases. Use manufacturer tables or software; larger pipes or a higher pump duty may be needed.
Remember
BS EN 806 covers domestic hot and cold potable water, not the main design of sealed heating circuits.

## Slide 24
Pipe sizing 2
01. Worked example
Example data
Design heat load: 8 kW
Flow temperature: 45°C
Return temperature: 40°C
ΔT: 5 K
Calculate the required flow
Q = ṁ × SHC × ΔT
ṁ = Q / (4.18 × 5)
ṁ = 8 / 20.9 = 0.383 kg/s
Flow rate = 0.383 L/s
0.383 × 60
= 23 L/min
02. Design checks
Before choosing the pipe, check:
Total pipe length and internal diameter.
Water velocity and pressure loss.
Bends, fittings, valves and filters.
Heat exchangers and manifolds.
Manufacturer minimum flow.
Circulation pump performance.
Only then confirm the pipe size.
03. Case study
System data
Heat loss = 8 kW
Required flow = 23 L/min
Primary pipework: 18 metres
Two magnetic filters and four motorised valves.
Problem: 22 mm pipe gives too much pressure loss.
Decision: Use 28 mm flow and return pipework to reduce resistance, steady the flow and help the pump work efficiently.
Notes: Tutor note
Ask learners:
"Why can't we simply use 22 mm because it worked with the previous gas boiler?"
Guide discussion towards:
Lower ΔT used by heat pumps.
Higher water flow rates.
Increased hydraulic resistance.
Manufacturer minimum flow requirements.
Learner takeaway
The correct pipe size is confirmed by engineering calculations—not by habit. Calculate the flow rate first, then verify velocity, pressure loss, pump duty and manufacturer requirements before selecting the final pipe diameter.

## Slide 25
Case study 1: ASHP retrofit
Scenario
Three-bedroom semi: calculated heat loss 7.6 kW at design condition; proposed 45°C flow.
Task
Compare manufacturer data: a nominal 8 kW unit may not provide 8 kW at the required outdoor temperature and flow temperature.
Key consideration
Select only when the verified output meets the calculated requirement.

## Slide 26
Case study 2: electrical and DNO
Scenario
Home has EV charger, induction hob, electric shower and proposed ASHP with 3 kW immersion.
Task
Identify supply, consumer-unit, maximum-demand and DNO checks before installation.
Key consideration
Do not assume the existing supply is adequate.

## Slide 27
Case study 3: solar and DHW
Scenario
Family of five: two showers and a large bath; south-west roof with partial shading.
Task
Identify DHW demand, cylinder/coil needs, PV versus solar-thermal considerations and control priorities.
Key consideration
Solar may reduce energy use but does not determine heat-pump size.

## Slide 28
Standards and evidence
Installation and design
Use current manufacturer installation/performance data and project design records.
Key references
MCS MIS 3005-D; BS EN 12831-1 heat-load principles; MCS 021 heat-emitter guidance; BS 7593 water treatment; ENA/DNO connection guidance.
Critical requirement
Always check current editions and local requirements.

## Slide 29
Knowledge check / summary
Plan the installation: survey, DNO, electrical supply, space, access, roof and siting.
Size the system from room heat loss, DHW demand, flow rate and pipework.
Select equipment using manufacturer performance at the calculated design conditions.
Choose from evidence, not assumptions or boiler ratings.

## Slide 30
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.