## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.38: System operation requirements to be checked for commissioning

## Slide 2: Introduction / Starter
Warm-up
What must be proven before a heat pump system is handed over?
Pair-share
Name three checks that could prevent a customer call-back.
Tutor Prompt
Commissioning proves the system is safe, clean, controlled and performing as intended.
Notes: Stop point: 3–5 minute discussion. Draw out flow/return temps, pressure, controls, water quality, safety and paperwork.

## Slide 3: Objectives (K1.38)
Identify the key operation requirements checked during commissioning
Explain why flow/return temperatures and pressure matter
Recognise control calibration, emitter distribution and pump checks
Describe hot water temperature and safety checks
Explain flushing, cleaning, chemical treatment and record keeping
Link commissioning evidence to customer handover and future maintenance
Notes: Learners should understand the purpose and evidence of each check, not just memorise a checklist.

## Slide 4: Commissioning: what are we trying to prove?
Safe manufacturer-limit operation
Confirms heat pump, cylinders, pumps, and valves operate within limits (BS EN 14336).
Correct Heat Transfer
Monitors temperatures, ΔT, and flow rate to identify issues like sludge or air.
Coordinated Control Sequence
Ensures thermostats and pumps operate in sequence to avoid cycling.
Correct Emitter Distribution
Ensures design intent for flow is met across all radiators/circuits (BS EN 12828).
Water Quality & Protection
Flushing and chemical checks to BS 7593:2019+A1:2024 to protect components.
Handover Evidence
Records of temperatures, pressures, and certificates support warranty and audits.
Notes: Tutor note: Commissioning is not just “turning the system on”. It proves the installation is safe, clean, controlled, balanced and documented. For heat pumps, this is especially important because small issues — poor flow, incorrect controls, dirty water, unsuitable ΔT or poor emitter distribution — can reduce efficiency and lead to customer complaints. Commissioning is the bridge between installation and reliable operation. Ask learners: what could happen if the system is installed but not commissioned?

## Slide 5: Flow and return temperatures
Stable Conditions
Measure when the heat pump is running steadily, not during start-up or shortly after a demand change.
Measurement Points
Readings must be taken at the correct points: primary circuit, cylinder circuit, buffer, or emitter circuit.
The Commissioning ΔT
System ΔT = flow temp − return temp. Note: This differs from emitter rating condition (ΔT50).
Target Expectations
Often ~5°C, but always check manufacturer specs. Aim is to confirm design intent, not force a specific number.
Large ΔT (Poor Flow)
Example: 13°C.Causes: low pump speed, blocked filters, air, poor balancing, or restricted exchanger.
Small ΔT (High Flow)
Example: 2°C. Causes: excessive flow, bypass mixing, short circuiting, or emitters not absorbing heat.
Evidence & Recording
Record temps, locations, mode, outdoor temp, and corrective actions. Provides a baseline for future maintenance and protects all parties.
Notes: Tutor depth:
System ΔT = flow temperature − return temperature. For heat pump systems, expected ΔT depends on manufacturer/design intent. Do not impose one fixed value; compare with design data and commissioning instructions.
Mini example:
Tutor example
A heat pump is being commissioned and the design expects approximately 5°C system ΔT during steady space-heating operation.
Reading 1: 45°C flow / 40°C return = 5°C
  This is close to the expected design condition.
Reading 2: 45°C flow / 32°C return = 13°C
  This suggests heat is not being moved away from the heat pump quickly enough. The engineer should check pump operation, system pressure, air removal, strainers/filters, valve positions and balancing.
Reading 3: 40°C flow / 38°C return = 2°C
  This may suggest excessive flow, bypassing, hydraulic mixing, or that emitters are not transferring enough heat at that moment. The system should be checked under stable load before deciding it is acceptable.
Learner takeaway
Flow/return temperature readings are diagnostic evidence. For heat pumps, a typical space-heating target may be around 5°C , but the correct value is always the one stated by the manufacturer/design documentation. Large or small ΔT values are not automatically “faults”, but they are clues that help confirm whether flow, heat transfer and controls are working correctly.

## Slide 6: System pressure and expansion checks
Fill & Static Pressure
Domestic sealed systems commonly have a cold fill pressure of 1.0–1.5 bar. This must suit the static height to prevent air ingress.
Follow manufacturer requirements
Suit system static height
Expansion & Safety
Check vessel pre-charge, sizing, and PRV rating. As the system heats, pressure should rise only within the expected safe range.
Watch for pressure loss/leaks
Verify PRV discharge
Evidence Recording
Record key commissioning data as evidence for compliance and future servicing.
Cold/hot pressure readings
Pre-charge & PRV ratings
Corrective actions
Scenario A: Acceptable Operation
Filled cold to 1.2 bar. Under load, pressure rises gradually to 1.6 bar. This is acceptable if within design instructions.
Scenario B: Pressure Issue
Filled cold to 1.2 bar, rises to 3 bar & discharges PRV. Suggests undersized/faulty vessel, overfill, or isolated vessel.
Notes: Tutor depth:
Incorrect pressure can cause air ingress, PRV discharge, low-pressure faults and corrosion risk. Heat pump systems may have added water volume from larger emitters, buffers or volumisers, so existing expansion arrangements must be checked.
Stop point: ask learners what pressure symptoms might appear if the expansion vessel is too small or incorrectly charged.

## Slide 7: Control system calibration and setup
Device Verification
Confirm thermostats, programmers, sensors and controllers read correctly and respond as intended.
Sensor Operation
Check weather compensation and outdoor sensor operation where fitted to ensure efficiency.
Logic & Setpoints
Verify setpoints, schedules, DHW priority and zone control logic against design specifications.
Requirement Match
Check controller settings match the design, manufacturer, and customer requirements to ensure comfort and compliance.
Evidence & Handover
Record key settings for handover and future servicing. Essential for maintaining the baseline and supporting maintenance.
Notes: Tutor depth:
Calibration means making sure controls measure/respond correctly. A sensor in the wrong location, wrong compensation curve or incorrect zone schedule can make the system appear faulty even if the hardware is fine.
Activity prompt: learners identify what could go wrong if the outdoor sensor is in direct sunlight.

## Slide 8: Heat emitter distribution and balancing
Emitter & Zone Checks
Confirm radiators, UFH loops, and fan convectors receive heat.
Verify thermostats/controllers open correct valves/circuits.
Flow Distribution
Heat pumps require steady flow. Poor distribution leads to high return temps or cycling.
Ensure sufficient flow to all circuits.
UFH loops, adjust flow top meters on individual loops in accordance with manufacturer design.
Radiator Balancing
Use strap-on thermometers to measure flow/return temp difference.
Adjust lockshield valves for suitable temp drop.
Open TRVs fully during process.
Investigate Poor Distribution
Check for trapped air, sludge/debris, blocked strainers, closed valves, incorrect pump settings or undersized emitters.
Evidence Recording
Record temp readings, UFH settings, and pump modes. This baseline proves commissioning and aids future maintenance.
UFH & Mixed Systems: Check manifold flow meters and ensure balanced operation so no single circuit dominates the system.
Notes: Tutor depth:
Low-temperature systems rely on steady distribution. A poorly balanced system may overheat nearby rooms and underheat distant rooms, forcing higher flow temperatures and reducing COP.
Stop point: Wordwall/Quizizz idea – 'Symptom → likely commissioning check'.

## Slide 9
Hot water temperature and DHW operation
Storage & Distribution
Stored water: ≥60°C for Legionella control.
Distribution: Reach ≥50°C within 1 min (≥55°C in healthcare).
Outlets & Blending
Record temp, time and location at set points.
TMV supply must reach ≥50°C within 1 minute.
Backup & Pasteurisation
Check immersion/backup heater boost where required: some heat pumps may not raise DHW to 60°C efficiently or independently, so an immersion heater / backup heater may be used for scheduled pasteurisation or anti-Legionella cycles.
Secondary Circulation
Consider loops for long runs to reduce waiting time. Ensure insulation and controls are fitted to minimise losses.
Record Keeping & Strategy
Confirm DHW priority, sensors, and recovery logic. Record all temps, settings, and guidance for handover.
Notes: Tutor depth:
For heat pump DHW systems, normal efficient stored hot water temperatures may be lower than traditional boiler systems, but Legionella control may require periodic raising of stored water to 60°C. Some heat pumps can achieve this directly, while others rely on an immersion heater or backup heater for the final temperature lift. Commissioning should confirm that the anti-Legionella/pasteurisation cycle is enabled, scheduled correctly, reaches the required temperature, and is explained to the customer. This also affects running cost, because immersion boost uses direct electric heating, so it should be controlled rather than left to operate unnecessarily.
Prompt: How could an incorrect cylinder sensor position affect DHW recovery?

## Slide 10: Circulation pump operation
Operational Status
Confirm pumps run when called and stop when appropriate.
Check pump direction, speed/mode and control signal.
Flow Verification
Verify required flow through all circuits:
Heat pump circuit
Zone circuits
Cylinder circuits
Performance Monitoring
Listen and check for system issues:
Noise or vibration
Cavitation
Trapped air
Data Recording & Balancing
Record all final pump settings and any balancing adjustments made during commissioning to ensure a verifiable baseline.
Notes: Tutor depth:
The pump must deliver the required flow against system resistance. Too little flow can cause high ΔT and flow faults; too much can cause noise and wasted energy.
Mini example: A blocked strainer causes low flow. The heat pump shows repeated flow alarms until the strainer is cleaned and the flow is rechecked.

## Slide 11: Safety checks before handover
Physical Safety
Confirm safety devices are fitted, accessible and correctly set.
Identification & Warning
Check isolators, labels, warning notices and emergency information.
Pressure & Discharge
Verify PRVs/discharge arrangements and expansion provision.
Competent Person Sign-off
Confirm electrical/refrigerant/gas/oil work is signed off by competent persons.
Handover Termination
Stop handover if safety-critical evidence is missing.
Notes: Tutor depth:
This is an awareness slide. Learners must not test/adjust regulated systems outside competence. The commissioning record should show safety-critical checks and any referrals/sign-offs.
Stop point: 'What would stop handover?' discussion.

## Slide 12: System flushing and cleaning
Cleaning Standards
Follow BS 7593:2019+A1:2024
Current code for preparation, commissioning and maintenance of water systems.
Water Regulations 1999
Prevent contamination and waste. Backflow prevention is critical (Fluid Cat 3).
Debris & Blockages
Remove: Flux, sludge, magnetite, and installation residues from pipe cutting/soldering.
Dirty Systems: Restrict flow, increase ΔT, cause noise, and lead to pump faults.
Strainers: Blocked filters cause low output and repeated lockouts.
Methodology
Cleaning must suit manufacturer instructions and system materials.
New install vs. conversion
Mixed metals/UFH
Glycol/brine circuits
Record Evidence for Warranty & Audit
Log what was cleaned, methods, chemicals, inhibitor/antifreeze dosing, filter checks, test results, and dates.
Notes: For heat pumps, clean system water is especially important because the system often relies on lower temperatures and stable flow rates. A dirty system may still “run”, but it may not transfer heat efficiently. A blocked strainer or plate heat exchanger can make the heat pump appear undersized or faulty when the real issue is poor water quality or restricted flow.
When discussing water regulations, remind learners that the heating circuit water is not wholesome water. If the system is connected to the mains for filling, suitable backflow prevention must be in place so heating water, chemicals or inhibitor cannot contaminate the drinking water supply.
Activity: identify components most vulnerable to debris (strainers, filters, plate heat exchangers, pumps, small valves).

## Slide 13
Chemical treatment and water quality
System Protection
Chemical treatment protects the system. Correct treatment helps prevent corrosion, scale, sludge, magnetite and biological growth, which reduce heat transfer and damage components.
Inhibitor & Glycol
Check inhibitor / antifreeze / glycol requirements
Heat pump systems, GSHP brine circuits, and frost-risk areas may require protection as specified by the manufacturer.
Compatibility
Confirm concentration & instructions
The product must be compatible with materials (heat pumps, emitters, valves). Incorrect concentration reduces protection and restricts flow.
Warranty Risk
Incorrect dosing may void warranty
Failure to dose correctly leads to corrosion and poor performance and may void manufacturer warranty.
Record Evidence: Include product name, concentration, test readings, dates, and system volume for warranty and audit purposes.
Notes: Tutor depth:
Incorrect treatment can damage components or void warranties. Glycol/antifreeze may be required in some external or ground-source circuits, but concentration must be correct.
Stop point: quick Q – what can too much glycol do to flow? (Higher viscosity/resistance, poorer flow, increased pump energy.)

## Slide 14: Documentation and records
Commissioning Records
Prove what was checked
Evidence that the system was inspected, tested, and left operating safely per manufacturer instructions..
System Settings
Record final operating state
Include temps, pressure, pump/control settings, DHW, weather compensation, and safety checks.
Water Treatment
Flushing and cleaning
Log methods, chemicals used, and test results. Links to BS 7593:2019+A1:2024.
Standards & Manuals
Manufacturer requirements
BS EN 14336 compliance. Manufacturer instructions are critical for model-specific procedures.
Benchmark Records
Industry standard checklists
Used to meet Part L Building Regulations. Complete on installation via app or manual.
Warranty Protection
Securing long-term support
Extended warranties require evidence of correct install and registration. Missing records affect support.
Variations & Certificates
Document design changes, unresolved issues, competence referrals, F-Gas evidence, and electrical certificates. Building regulations approval, self-certification through a competent persons scheme, and MCS approval.
Future Fault-Finding
Commissioning records create a baseline for future engineers to diagnose changes in system performance.
Notes: Tutor depth:
Documentation is part of commissioning, not an admin afterthought. If it is not recorded, it is difficult to prove what was done.
Examples: commissioning checklist, handover sheet, electrical certificate, F-Gas referral note, water treatment record, customer control guidance.

## Slide 15: Worked example: interpreting commissioning readings
Scenario & Readings
ASHP designed for steady, low-temp heating.
Flow/Return: 45°C / 33°C (ΔT: 12°C)
Obs: Distant radiators are cool
Risk: Rooms may not hit design temp
What does this suggest?
Heat is not being distributed evenly.
12°C ΔT suggests flow rate is too low.
Water takes the easiest route, starving distant circuits.
Post-Correction Recheck
After cleaning, air removal & balancing:
Flow: 45°C / Return: 40°C (ΔT: 5°C)
Obs: All radiators heat evenly
Outcome: Suitable for handover
Notes: Tutor guide: this is slide one out of two for this example.
This example shows why flow/return readings are not just numbers. A high ΔT and cool emitters can point toward insufficient flow or distribution problems.
Learner output: list three checks they would complete before escalating. Suggested answers: check pump running/mode, valve positions, air removal, filter/strainer cleanliness, balancing, pressure.

## Slide 16: Worked example: interpreting commissioning readings
Possible Causes to Investigate
Low Flow Rate: Check pump speed, mode & resistance.
Air in System: Air locks at high points; check vents.
Blocked Strainer: Installation debris or sludge.
Poor Balancing: Nearby circuits taking too much flow.
Control Issues: Incorrect valve positions (TRVs/Lockshields).
Engineer Actions
Investigate: Check pressure, pump settings, and use clamp probes to compare radiator temps.
Balance: Fully open TRVs, adjust lockshields for even distribution, and recheck after each change. UFH, check flow top meters and adjust to the manufacturer-stated flow rate for loop.
Escalate: Refer design faults, undersized pipes, or electrical issues to relevant specialist.
Record: Document initial readings, all checks, adjustments, and final verified performance.
Notes: Tutor guide:
This example shows why flow/return readings are not just numbers. A high ΔT and cool emitters can point toward insufficient flow or distribution problems.
Learner output: list three checks they would complete before escalating. Suggested answers: check pump running/mode, valve positions, air removal, filter/strainer cleanliness, balancing, pressure.

## Slide 17: Activity: commissioning checklist review (15 mins)
Using a sample checklist, identify the evidence needed for each section:
Thermostat
flow/return temperatures and pressure
Settings
controls, emitters and pump operation
Hot tub
DHW temperature and safety checks
Assignment
flushing, treatment and records
Output: mark which items are Pass / Investigate / Refer
Notes: Workbook task created by others.
Tutor circulates and checks learners are linking evidence to reasons, not just ticking boxes.
Stop point: compare answers.

## Slide 18: Video / demonstration break
Topic
Commissioning sequence and why records matter.
Watch
Short manufacturer/industry commissioning clip.
Discuss
What checks were visible and what evidence would be recorded?
Stop point: identify one check you would never skip
Notes: Paste chosen video link here (notes only) and mirror in SoW.
Watch YouTube video.
https://www.youtube.com/watch?v=cYRuxOtNtdU
Suggested sources: manufacturer training channels or Heat Pump Association content. Do not place link on slide.

## Slide 19: Recap checkpoint
Question 1
Why do flow and return temperatures matter?
Question 2
What can cause unstable system pressure?
Question 3
Why is flushing/chemical treatment important?
Question 4
What commissioning records support future maintenance?
Stop point: Wordwall/Quizizz recap
Notes: Suggested answers:
1) They show heat transfer and flow performance.
2) Leaks, incorrect fill pressure, vessel issues, PRV discharge, air.
3) Prevents debris, corrosion, blockage and poor heat transfer.
4) Temperatures, pressures, pump/control settings, water treatment, safety checks, certificates.

## Slide 20: Summary & Questions
Purpose
Commissioning proves the system operates safely and as designed.
Protection
Water cleanliness and chemical treatment protect long-term performance.
Key Checks
Temperatures, pressure, controls, emitters, DHW, pumps, and safety systems.
Essential Records
Vital for handover, warranty, audits, and future fault-finding.
Notes: Final tutor prompt: Ask learners to explain commissioning in one sentence: 'Commissioning is…'.

## Slide 21
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.