## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.39: Inspection techniques for commissioning

## Slide 2: Introduction / Starter
Warm-up
What can you discover before switching the system on?
Pair-share
List visible clues that an installation is not ready for commissioning.
Tutor Prompt
'Inspection is the first safety and quality filter before testing.’
Notes: Stop point: 3–5 minute discussion. Draw out leaks, unsupported pipework, missing insulation, incorrect siting/clearances, labels, dirty filters, poor condensate route, wiring concerns, missing documentation.

## Slide 3: Objectives (K1.39)
COMMISSIONING PURPOSE
Explain the purpose of inspection before commissioning.
SENSORY TOOLS
Use senses appropriately: sight, sound, touch and smell.
VISUAL INSPECTION
Carry out visual inspection at awareness/application level.
LOW CARBON SYSTEMS
Identify pre-commissioning checks for low carbon systems.
REPORTING PROTOCOL
Know when to stop, record and refer.
MANUFACTURER GUIDANCE
Use manufacturer instructions to guide inspection.
Notes: Learners should understand what can be inspected visually, what must not be touched/altered without competence, and why manufacturer instructions define the exact inspection requirements.

## Slide 4: Inspection: what are we trying to prove?
READY FOR TESTING
Installation complete and safe
Inspection is the first check for obvious safety or quality issues before commissioning.
RELEVANT REQUIREMENTS
Alignment with standards
Consistent with instructions, British Standards, Building Regs, MCS, and design specs.
COMPONENTS & DESIGN
Correct location and access
Heat pumps, valves, and wiring must match design and be accessible for maintenance.
PROTECTION & CLEARANCE
Manufacturer specs met
Confirm airflow, vibration protection, insulation, frost protection, and warning labels.
CONDITION CHECKS
No leaks or damage
Look for water leaks, corrosion, blocked filters, trip risks, or signs of overheating.
REPORTING PROTOCOL
Issues recorded early
Record, classify, and correct any defects or non-compliance before testing begins.
Notes: Tutor note: K1.39 comes before K1.40 testing. Inspection identifies whether it is safe and sensible to proceed to tests. If inspection finds a safety-critical issue, stop and escalate before testing.

## Slide 5: Using senses safely in inspection
SIGHT — MAIN METHOD
Check layout, location, leaks & labels.
Example: spotting missing pipe insulation on external ASHP pipework.
SOUND — ABNORMAL OPERATION
Listen for air, cavitation or rattling.
Example: a rattling outdoor unit may indicate poor mounting.
TOUCH — WITHIN COMPETENCE
identify vibration & surface temps.
Caution: Do not touch live parts or hot surfaces.
SMELL — HIDDEN PROBLEMS
Signs of overheating or chemicals.
Example: a burning smell near controls means stop immediately.
LIMITATIONS
Senses do not replace proper testing.
Cannot prove pressure integrity, electrical safety, or calibration.
UNSAFE SIGNS?
Stop, Record and Refer.
Do not "work around" unsafe signs. Escalate to competent person.
Notes: Tutor depth:
Senses support inspection, but they do not prove compliance alone. Do not encourage learners to touch live electrical parts, refrigerant pipework, hot surfaces or unsafe components. Use tools and competent persons where required.
Quick question: which sense might identify a blocked condensate route? Sight (pooling/ice), smell (stagnant water), sound (gurgling) depending on context.

## Slide 6: Visual inspection: external unit and siting
LOCATION & AIRFLOW
Manufacturer compliance
Check unit location against manufacturer clearances and airflow requirements.
STABILITY & FIXINGS
Secure installation
Look for level base/brackets, vibration control and secure fixings. Ground Source – ensure ground loops have been installed in accordance with design specification, similar to bore hole depth.
SERVICE ACCESS
Maintenance readiness
Check service access and ensure a safe working area is available.
WATER & DRAINAGE
Condensate management
Inspect defrost water route and assess freeze/slip risk in the area.
PHYSICAL CONDITION
Visual damage checks
Check for blocked grilles, debris, poor drainage, or visible damage.
REPORTING
Record concerns
Record siting concerns before commissioning continues.
Notes: Tutor note:
For ASHPs, poor siting can reduce airflow, increase noise, cause recirculation of cold air and create drainage/freeze risks. Manufacturer instructions set clearances and service access requirements.
Stop point: show an image of an outdoor unit and ask learners to identify inspection points.

## Slide 7: Visual inspection: pipework and insulation
ROUTE & PROTECTION
Structural Integrity
Check pipework route, supports, clipping and protection from damage.
INSULATION
Weatherproofing
Confirm insulation is fitted where required and weatherproof externally (e.g. Armaflex rubber).
INTEGRITY CHECK
Leaks & Corrosion
Look for leaks, corrosion, poor joints, kinks or stressed pipework.
VALVES & POSITION
Accessibility
Check isolation/service valves are accessible and correctly positioned.
MAINTENANCE POINTS
Service Access
Confirm drain points, vents and strainers are accessible for commissioning/service.
REPORTING
Documentation
Record defects and do not hide issues behind insulation or boxing-in.
Notes: Tutor depth:
Pipework inspection should consider both mechanical integrity and future maintainability. Heat pump systems often rely on stable flow, so restrictions, poor insulation and inaccessible filters can affect performance.
Activity: learners identify pipework issues from a photo/diagram (created separately).

## Slide 8: Visual inspection: cylinders, stores and DHW components
PLACEMENT & ACCESS
Location & Support
Check cylinder/store location, support and service access.
SAFETY DEVICES
Discharge & Expansion
Confirm visible safety devices, discharge routes and expansion provision.
COMPONENTS
ID & Insulation
Check pipe identification, insulation, valves and sensor positions.
CIRCULATION
Valves & TMVs
Inspect TMVs/blending valves and secondary circulation where fitted.
CONDITION
Physical Defects
Look for leaks, corrosion, loose fittings or missing labels.
REGULATIONS
G3 Compliance
Refer regulated checks where competence is required (G3 Building regulations).
Notes: Tutor note:
Keep unvented cylinder safety at awareness level. Do not ask learners to certify regulated work unless they are competent/authorised. The inspection should identify whether safety components are present, accessible and recorded, then refer where required.
Prompt: why is cylinder sensor position important for DHW recovery?

## Slide 9: Visual inspection: emitters and distribution circuits
CONNECTION & ACCESS
Accessibility
Check radiators, UFH manifolds and fan convectors are connected and accessible.
COMPONENT CONDITION
Visual Check
Look for air vents, leaks, valve positions, flow meters and actuator condition.
ZONING
Intended Use
Confirm emitters match the intended zones/rooms.
UFH SYSTEMS
Labels & Flow
Check UFH loop labels and manifold flow meters where fitted.
PHYSICAL INTEGRITY
Support & Airflow
Look for signs of poor support, damage, corrosion or blocked airflow.
RECORDING
Documentation
Record issues before balancing and operational testing.
9
Notes: Tutor depth:
The inspection stage checks whether distribution components are physically ready. K1.40/K1.38 then prove operation through flow/temperature/balancing checks.
Stop point: learners list three inspection checks on a UFH manifold.

## Slide 10: Visual inspection: controls and sensors
DEVICES & ACCESS
Fitted & Accessible
Check thermostats, programmers, controllers and sensors are fitted and accessible.
EXTERNAL SENSORS
Location & Exposure
Confirm outdoor sensor location is suitable and not obviously affected by heat/sun.
WIRING & COVERS
Visual Verification
Check wiring routes, labels and protective covers visually only.
VALVES & STRATEGY
Control Matching
Confirm zone valves/actuators match the control strategy.
INTEGRITY
Labels & Fixings
Look for missing labels, loose devices or incorrect placement.
RESTRICTIONS
Competence Limits
Do not alter fixed wiring unless competent/authorised.
Notes: Tutor note:
Controls often cause performance issues. A sensor in direct sunlight or above a heat source can mislead the system. Inspection should check location and obvious installation quality before calibration/operational testing.
Activity prompt: what happens if the outdoor sensor is mounted in direct sunlight?

## Slide 11: Visual inspection: electrical and competence boundaries
PRESENCE & ACCESS
Checklists
Check isolators, labels, warning notices and access are present.
DAMAGE & RISKS
Visual Faults
Look for obvious damage, missing covers, unsupported cables or water ingress risk.
CERTIFICATION
Compliance
Confirm electrical work has suitable certification/competent sign-off where required.
LIMITS OF WORK
Competence
Do not open live equipment or carry out tests outside competence; refer to safe isolation procedure.
REPORTING
Escalation
Record concerns and refer to electrician or electrical designer.
SAFETY ROLE
Scope
Inspection supports safety but does not replace formal electrical testing.
Notes: Tutor depth:
This slide is awareness and boundary setting. Learners need to know what to look for and when to refer, not how to complete electrical testing unless qualified.
Link to K1.8 limits of competence and K1.13 electrical supply awareness.

## Slide 12: Visual inspection: water quality and cleanliness clues
CONTAMINATION
Debris & Sludge
Look for dirty filters/strainers, sludge, debris or contaminated water.
MAINTENANCE ACCESS
Points & Filters
Check flushing points, dosing points and magnetic filters are accessible.
LEAK INSPECTION
Equipment Health
Inspect for leaks around treatment equipment and strainers.
DOCUMENTATION
Handover Evidence
Confirm chemical treatment evidence is available before handover.
FLUID RECORDS
Glycol/Antifreeze
Check glycol/antifreeze labels or records where applicable.
ACTION TRIGGERS
Testing & Cleaning
Poor water quality clues should trigger testing/cleaning checks.
Notes: Tutor note:
Visual inspection cannot prove water quality alone, but it can reveal warning signs. Link to BS 7593 principles and K1.38 chemical treatment/water quality checks.
Prompt: why could a blocked strainer make a heat pump appear faulty?

## Slide 13: Pre-commissioning checks: before energising/starting (slide 1/2)
DOCUMENTATION & DESIGN
Manufacturer Instructions
Confirm manuals, wiring, drawings, and MCS evidence are on site. Match installed system to design intent.
HYDRAULIC STATUS
Filling & Pressure
System filled, air removed from all high points. Confirm pressure matches requirements; do not start if low/unstable.
ACCESSIBILITY
Service Points
Ensure valves, strainers, and pumps are reachable. Check isolation valves and pump orientation.
REGULATED TASKS
Sign-offs & Compliance
Confirm electrical, refrigerant, and unvented sign-offs. Do not energise if safety evidence is missing.
ENVIRONMENTAL
Drainage & Frost
Check condensate routes and fall. Confirm glycol/antifreeze and trace heating are fitted as specified.
WATER QUALITY
Treatment Evidence
Confirm flushing/cleaning complete. Ensure inhibitor is added and testing evidence is recorded.
Notes: Tutor note:
Manufacturer instructions are model-specific and may contain limits that are more precise than general guidance. Learners should practise finding critical information quickly in manuals.
Activity: manual-reading task — find three pre-commissioning checks in a heat pump manual.

## Slide 14: Pre-commissioning checks: before energising/starting (slide 2/2)
COMPONENTS
Visual Integrity
Check insulation, supports, joints, and emitters. Look for leaks, damage, or incorrect valve positions.
CONTROLS
Sensor Positioning
Check thermostats and sensors are located correctly. Poor location leads to false readings and cycling.
STOP IF NOT READY
Safety first: Record and correct any issues affecting safety, warranty, or compliance before energising.
Notes: Tutor note:
Manufacturer instructions are model-specific and may contain limits that are more precise than general guidance. Learners should practise finding critical information quickly in manuals.
Activity: manual-reading task — find three pre-commissioning checks in a heat pump manual.

## Slide 15: Inspection findings: record, classify and act
Record
Record what was inspected, condition found and evidence/photos if permitted
Classify
Pass / Monitor / Correct before commissioning / Refer
Act
Correct minor issues within competence and retest/reinspect
Next Steps & Compliance
Refer safety-critical or regulated issues to competent persons
Document limitations, variations and outstanding actions
Do not proceed to commissioning if a critical inspection item fails
Notes: Tutor depth:
Good inspection is evidence-based. Avoid vague wording like 'looks okay' where a specific observation is better.
Example record: 'ASHP base level; 300 mm rear clearance measured; condensate route incomplete — commissioning paused pending drain completion.'

## Slide 16: Scenario: visual inspection before ASHP commissioning
Scenario Context
ASHP installed and customer wants handover today. Inspection identifies specific findings that must be addressed.
Inspection Findings:
Incomplete condensate route
Blocked rear clearance
Missing water treatment record
Task: Classification
Decide Pass / Correct / Refer for each finding based on severity and competence requirements.
Task: Explanation
Explain which commissioning tests should be paused due to the failed inspection items.
Output Requirements
Create an inspection action list and a formal customer communication note.
Notes: Suggested approach:
- Condensate route incomplete: correct before handover; may affect defrost water safety.
- Blocked rear clearance: correct or refer to installer/designer; may affect airflow/performance.
- Missing water treatment record: investigate and document before handover; warranty/performance risk.
Workbook task created separately.

## Slide 17: Activity: senses-based inspection walkaround
Using a photo pack or training rig, inspect using:
Sight
leaks, labels, access, damage, insulation
Sound
vibration, loose parts, air/noise where running safely
Touch
safe vibration and temperature checks only
Smell
burning, chemicals, stagnant water or overheating signs
Create a short Pass / Correct / Refer report
Notes: Tutor note:
Photo pack/training rig created separately. Reinforce safety boundaries: no touching unsafe surfaces, live electrical parts, refrigerant components, or anything outside competence.
Stop point: groups compare findings and justify why they would proceed or pause commissioning.

## Slide 18: Recap checkpoint
01
Name four things checked during a visual inspection.
02
Why must manufacturer instructions be used before commissioning?
03
Give one safe use of sight, sound, touch and smell.
04
What should happen if an inspection finds a safety-critical issue?
05
What is the purpose of pre-commissioning checks?
Review the topics covered in K1.39 to ensure your understanding before proceeding.
Notes: Suggested answers:
1) Clearances, leaks, pipe supports, labels, insulation, sensors, valves, access, drainage.
2) They define model-specific limits, prerequisites and commissioning requirements.
3) Sight: leak/damage; sound: vibration/noise; touch: safe vibration check; smell: burning/chemicals.
4) Stop, record, refer/correct before commissioning.
5) To confirm the system is safe/ready before active testing and handover.
Wordwall/Quizizz recap created separately.

## Slide 19: Summary and questions
Key Takeaways
K1.39 focuses on inspection before and during commissioning
Senses support inspection but do not replace proper testing
Visual inspection identifies safety, quality and readiness issues
Pre-commissioning checks must follow manufacturer instructions
Record findings clearly and stop/refer where limits of competence apply
Notes: Final prompt: ask learners to explain why inspection is important in one sentence: 'Inspection is important because…'.

## Slide 20
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.