## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.40: Testing techniques for commissioning

## Slide 2: Introduction / Starter
Warm-up
What is the difference between installing a system and proving it works?
Pair-share
Name three tests/checks completed before handover.
Tutor Prompt
Testing is evidence that the system is safe, sound and operating as designed.
Discussion Focus: Quality Assurance & Safety Compliance
Notes: Stop point: 3–5 minute discussion. Draw out soundness testing, hydraulic pressure testing, temperature/flow/pressure checks, controls checks and safety component operation.

## Slide 3: Objectives
Testing Techniques
Identify testing techniques used when commissioning low carbon systems
Air vs. Hydraulic
Explain when air testing or hydraulic pressure testing may be suitable
Soundness Testing
Sequence: fill, stabilise, pressure test, and leak check
Operational Checks
Recognise checks: temperature, flow rate, pressure, and controls
Safety & Performance
Explain safety component and performance testing
Waste Disposal
Describe safe handling and disposal of test by-products
eduqas | eal | Engineering Group
Notes: Learners should understand suitability/application of each test and how evidence is recorded, not just list test names.

## Slide 4: Testing: what are we trying to prove?
Integrity
Pipework and components are sound and leak-free
Pressure
The system holds pressure under the required test conditions
Design Values
Temperatures, flow rates and pressures match manufacturer expectations
Controls
Controls and safety components operate in the correct sequence
Safety
The system performs safely before handover to the client
Waste Management
By-products from testing/cleaning are handled and disposed of safely
Notes: Tutor note: link K1.40 to K1.38 and K1.41. K1.38 = what operation requirements are checked. K1.40 = techniques used to test. K1.41 = records proving completion.
Standards/context: testing must follow manufacturer instructions, current industry standards and site procedures. Mention BS EN 14336 for installation/commissioning of water-based heating/cooling systems and BS 7593 for water system preparation/cleaning/treatment.

## Slide 5
Test planning: before any test starts
Test Scope
Confirm scope: pipework, heat pump circuit, DHW and emitter circuits
Information Check
Review manufacturer instructions, design data, and required test pressures
Isolation
Identify components requiring isolation or protection during testing
Equipment & Access
Use calibrated gauges and establish safe access methods
Safety Controls
Define exclusion zones, PPE, competent personnel, and escalation routes
Recording
Confirm the protocol for recording and documenting test results
Notes: Tutor depth:
Do not assume one pressure test suits every circuit. Heat pump systems may include plastic pipework, UFH manifolds, valves, strainers, cylinders, heat exchangers, buffer vessels and sensitive controls. Some components may have maximum test pressures or must be isolated.
Prompt: 'Why might manufacturer instructions override a generic test assumption?'

## Slide 6: Soundness testing: core sequence
1) Prepare system/section
Confirm test medium and pressure
Isolate/protect sensitive components
Fit blanking caps and gauges
2) Initial fill
Fill slowly using water
Vent air from all high points
Check for obvious leaks
3) Stabilisation period
Allow pressure/temp to settle
Account for air/expansion movement
Re-vent and recheck pressure
4) Raise to test pressure
Use specified duration/pressure
Increase pressure gradually
Isolate test pump/source
5) Inspect for leaks
Visually inspect all joints/emitters
Look for drops or damp patches
Repair and repeat if leak found
6) Check after test period
Verify pressure within tolerance
Investigate any pressure drops
Do not simply top up
7) Record the result
Record: circuit, medium, pressures, times, leaks found, repairs made, and personnel.
Status: Pass / Investigate / Fail / Retested and Passed
Notes: Tutor note:
Soundness testing proves pipework/components are leak-tight before the system is relied upon. The exact test pressure/duration must come from manufacturer instructions, design specification, pipe manufacturer guidance and current industry practice.
Stop point: learners put soundness test steps in the correct order.

## Slide 7: Soundness testing: Scenario
Scenario
An ASHP is being installed with a new low-temperature radiator circuit and a buffer vessel. Before commissioning, the installer must prove the wet heating pipework is sound.
Test procedure example 1 of 2:
1. Information Check: The engineer checks the heat pump manual, pipework specification and component pressure ratings.
2. Isolation: The heating circuit is isolated from any components that must not be exposed to the test pressure.
3. Fill & Vent: The circuit is slowly filled with water and air is vented from radiators, high points and the buffer vessel.
4. Stabilise: The system is allowed to stabilise. Pressure is checked again after air removal.
Notes: Tutor note:
Soundness testing proves pipework/components are leak-tight before the system is relied upon. The exact test pressure/duration must come from manufacturer instructions, design specification, pipe manufacturer guidance and current industry practice.
Stop point: learners put soundness test steps in the correct order.

## Slide 8: Soundness testing: Scenario
Test procedure example 2 of 2:
5. Pressurise: The circuit is raised to the specified test pressure using a hydraulic test pump.
6. Inspect: The engineer inspects all accessible joints, radiator valves, manifolds, drain points and buffer connections.
7. Fault Found: A small weep is found on a compression joint near a radiator. The test is stopped, the circuit is depressurised safely, the joint is remade, and the test is repeated.
8. Success: On retest, the pressure remains stable for the required test period.
9. Record: The engineer records the final pressure, test duration, repair made and retest pass result in the commissioning documentation.
Notes: Tutor note:
Soundness testing proves pipework/components are leak-tight before the system is relied upon. The exact test pressure/duration must come from manufacturer instructions, design specification, pipe manufacturer guidance and current industry practice.
Stop point: learners put soundness test steps in the correct order.

## Slide 9: Initial fill and stabilisation
Controlled Fill
Fill slowly to reduce air locking and water hammer risk
Venting
Vent radiators, UFH manifolds, high points, pumps and heat exchangers
Pressure Check
Check fill pressure against design and static height requirements
Stabilisation
Allow temperature and pressure to stabilise before taking test readings
Filtration
Check strainers and filters after flushing or filling where required
Recording
Record fill pressure and any air removal issues encountered
Notes: Tutor depth:
Air affects pressure readings and can create false test results. Temperature changes can also affect pressure during the test. Stabilisation is part of producing a reliable result, not wasted time.
Ask learners: what could give a false pressure drop during a test? Suggested: trapped air, temperature change, gauge issue, loose test hose, small leak.

## Slide 10: Hydraulic pressure testing 1 of 2
What & Where it is Used
Hydraulic pressure testing uses water to test pipework for soundness before commissioning.
Used on wet heating, low carbon pipework, and UFH manifolds.
Preferred over air as water is less compressible (lower risk).
Proves system can hold pressure without leakage.
Standards & Regulations
BS EN 14336: Installation and commissioning requirements.
BS 7593:2019+A1:2024: Preparation and maintenance.
Water Regs 1999: Prevents contamination and waste.
Requires suitable backflow prevention when mains filling.
Always follow manufacturer instructions for exact test pressure and permitted methods.
Notes: Tutor depth:
Hydraulic testing is usually preferred for many wet systems because water is far less compressible than air. However, it can still cause damage or flooding if not controlled. Isolate sensitive equipment if required, and do not exceed component pressure ratings.
Hydraulic pressure testing is often safer than air testing because water does not store energy in the same way compressed air does. However, it still needs control: too much pressure can damage components, and poor venting can give misleading results. For low carbon heating systems, the test must also consider sensitive components such as heat exchangers, UFH manifolds, valves, filters, buffer vessels, cylinders and heat pump modules.
The key teaching message is: test the right section, at the right pressure, for the right duration, using the right method — then record the evidence.
Mention: if water contains chemicals, inhibitor or glycol, disposal must be controlled and not discharged irresponsibly.

## Slide 11: Hydraulic pressure testing 2 of 2
Basic Test Sequence & Safety
Isolate/protect components from excessive test pressure.
Fill slowly, vent air from high points/emitters, and stabilise.
Raise to required pressure using pump/calibrated gauge.
Visually inspect all joints; repair defects and retest.
Safe Disposal: Contaminated water (glycol, sludge) must follow site procedures.
Evidence: Record fill/test pressure, duration, and person.
Always follow manufacturer instructions for exact test pressure and permitted methods.
Notes: Tutor depth:
Hydraulic testing is usually preferred for many wet systems because water is far less compressible than air. However, it can still cause damage or flooding if not controlled. Isolate sensitive equipment if required, and do not exceed component pressure ratings.
Hydraulic pressure testing is often safer than air testing because water does not store energy in the same way compressed air does. However, it still needs control: too much pressure can damage components, and poor venting can give misleading results. For low carbon heating systems, the test must also consider sensitive components such as heat exchangers, UFH manifolds, valves, filters, buffer vessels, cylinders and heat pump modules.
The key teaching message is: test the right section, at the right pressure, for the right duration, using the right method — then record the evidence.
Mention: if water contains chemicals, inhibitor or glycol, disposal must be controlled and not discharged irresponsibly.

## Slide 12: Air testing: suitability and limitations
What air testing is used for
Air testing uses compressed air or an inert gas to identify leaks before water is introduced.
Used during staged installation or to prevent damage to finishes/insulation.
Pros of air testing
High water damage risk areas.
Staged installation leak detection.
Avoids frost risk in cold weather.
Cons and limitations
Hazardous stored energy release.
No flushing or flow verification.
Small leaks behave differently.
Process Overview
Isolate and cap pipework section.
Connect controlled air source and gauges.
Pressurise slowly; monitor for drops.
Inspect joints with leak detection fluid.
Safety Controls & Escalate
Never use oxygen: fire/explosion risk!
Use calibrated gauges and relief valves.
Keep personnel away from temporary caps.
Stop if pressure or scope is unclear.
Safety and adherence to manufacturer instructions are paramount during air testing.
Notes: Tutor depth:
Compressed air stores energy and a failure can be violent. This is why air testing must be controlled and competence/safe procedure matters. For many heating systems, hydraulic testing is preferred where suitable.
For learners, the key point is that air testing can be useful, but it is not the default answer for every system. It may be suitable for checking a section of pipework before filling, especially where water damage would be costly. However, because air is compressible, it stores energy. If a temporary cap, joint or fitting fails, it can fail violently.
Hydraulic testing with water is often safer from a stored-energy point of view, but it introduces water, so it needs drainage, frost and building-damage risks considered. The correct method depends on the system, manufacturer instructions, pipe material, site conditions and competence.
Activity prompt: learners compare air vs. hydraulic testing — which is safer for stored energy, and which may reduce water damage risk?

## Slide 13
Leak checking and pressure after test period
Inspection
Check all accessible joints, valves, manifolds, emitters and equipment connections using visual inspection and suitable leak detection methods.
Monitoring
Monitor the gauge at the start, during and end of the test period to ensure system stability.
Investigation
Investigate any pressure drops: check for leaks, trapped air, temperature changes or equipment issues.
Rectification
Repair and retest according to instructions and competence boundaries if issues are identified.
Recording
Record final pressure and clearly document the pass/fail decision for the commissioning file.
Thorough post-test verification is essential for ensuring long-term system integrity.
Notes: Tutor note:
A pressure drop is not automatically a leak, but it must be investigated. Retesting after repair is essential.
Prompt: what information should be recorded after a failed test? Suggested: initial pressure, final pressure, duration, area tested, fault found, repair, retest result and person responsible.

## Slide 14
Operational checks: temperature, flow, pressure and controls
Temperature
Confirm flow/return, DHW and outlet temperatures where relevant.
Flow Rate
Verify required flow through heat pump, zones and cylinder circuits.
Pressure
Confirm stable cold and hot operating pressures.
Controls
Check sensors, thermostats, zone valves, DHW priority and safety interlocks.
Conditions
Readings must be taken under suitable operating conditions.
Documentation
Record values and compare with design/manufacturer expectations.
Comprehensive operational checks ensure system reliability and efficiency.
Notes: Tutor depth:
Operational testing is different from soundness testing. A system can be leak-free but still perform poorly if flow is wrong, controls are misconfigured or temperatures are outside design expectations.
Tie to K1.38 slides: flow/return ΔT, pump operation, DHW temperatures, water quality and controls.

## Slide 15: Flow rate testing and proving heat transfer
Measurement Methods
Flow can be checked using heat pump data, flow meters, balancing valves or commissioning tools.
Verification
Compare measured flow with design/manufacturer requirements.
Low Flow Impacts
Can cause high ΔT, flow alarms, poor output or short cycling.
High Flow Impacts
Can cause noise, poor balancing or unnecessary pump energy.
Pre-Check Actions
Check strainers, air, valves, pump mode and balancing before changing design settings.
Documentation
Record method used and final flow/balancing settings.
Operational efficiency depends on precise flow rate verification and proving.
Notes: Tutor example:
An 8 kW heat pump designed for a 5K system ΔT needs around 23 L/min. If measured flow is much lower, investigate pump mode, blocked strainer, closed valves, air, pipe resistance and balancing.
Learner task: identify three causes of low flow before escalating.

## Slide 16
Controls testing
Zoning & Function
Check each thermostat/controller calls for the correct zone or function.
Sequence of Operation
Verify zone valves, pumps and heat pump enable signals operate in sequence.
DHW Priority
Test DHW priority and return to space heating after cylinder demand.
Sensors & Compensation
Confirm weather compensation/outdoor sensor readings are plausible.
Settings Verification
Check user-accessible settings vs. installer/service settings.
Handover & Recording
Record final settings and explain key controls at handover.
System baseline: Accurate control settings are essential for efficiency and user comfort.
Notes: Tutor note:
A control fault can look like a heat pump fault. Learners should understand sequence testing: demand → valve/pump → heat source → feedback/sensor → stop/reset.
Stop point: ask learners what could happen if a cylinder sensor is incorrectly positioned or a zone valve is wired incorrectly.

## Slide 17: Safety component operation
Fitting & Access
Confirm required safety devices (PRVs, expansion vessels, isolators) are present, correctly located, and accessible for servicing.
PRVs & Discharge
Check PRV ratings and ensure expansion vessels are pre-charged. Discharge pipework must terminate safely and visibly.
Isolation & Frost
Service valves must be accessible and labelled. Confirm frost protection strategies (trace heating, glycol) for ASHPs are in place.
Temp & Overheat
Confirm high-limit controls and blending valves are set correctly. This links to safe DHW delivery and Legionella control.
Pressure Protection
Maintain water pressure within design range. Refrigerant pressure protection requires specialist F-Gas qualifications.
Prohibited Acts
NEVER bridge sensors, override alarms, isolate relief valves, or defeat safety devices. A bypassed system is unsafe.
Record Evidence: If a safety-critical item is missing or unverified, stop commissioning until resolved.
Notes: Tutor depth:
Safety component operation must be tested/verified in line with manufacturer instructions and competence boundaries. Do not teach learners to defeat safety devices.
Examples: PRV/discharge arrangement inspection; expansion vessel/pre-charge evidence; unvented cylinder controls by competent person; F-Gas safety limits/referrals for refrigerant circuit issues.

## Slide 18: Performance testing
Design Intent
Performance testing checks that the system matches design, manufacturer instructions, and customer requirements.
Design Values
Check operation against design: flow/return temp (e.g. 45°C/40°C), ΔT, flow rate, and control strategy.
Heat Delivery
Confirm radiators and UFH loops receive heat evenly. Poor distribution reduces efficiency.
DHW & Hydraulics
Verify DHW priority and cylinder heating. Check for noisy pipework or short cycling.
ASHPs Specifics
Observe defrost cycles. Ensure condensate water drains safely without causing hazards.
Adjust & Escalate
Adjust settings within competence. Escalate design issues like undersized emitters.
Record Evidence: Create a baseline for future servicing and fault-finding.
Notes: Tutor depth:
Performance testing is not always a full seasonal efficiency assessment. It is a commissioning check that the system is capable of operating as designed at the time of handover.
An ASHP is commissioned on a mild day. The heat pump runs, but performance testing shows frequent cycling, a high flow/return ΔT, and two radiators at the far end of the circuit remain cool. The system is not ready for handover just because the heat pump turns on.
The engineer checks pump mode, pressure, air removal, strainers, valve positions and balancing. After cleaning the strainer and balancing the radiators, the system runs for longer periods, the ΔT moves closer to design intent, and all rooms receive heat more evenly. The corrected readings and final settings are recorded in the commissioning paperwork.
Learner takeaway
Performance testing proves useful operation, not just basic operation. A heat pump system must deliver heat and hot water safely, efficiently and consistently — with evidence recorded before handover.
Prompt: what evidence would show a heat pump is not performing correctly? Suggested: repeated cycling, high ΔT, low flow, cold emitters, poor DHW recovery, nuisance faults, high flow temperature needed.

## Slide 19: Testing by-products: safe disposal
Pre-Work Requirement
Identify by-products before testing/cleaning starts.
Common Examples
Flush water, dirty water/sludge, chemicals, inhibitor, glycol/brine.
Compliance & Safety
Do not discharge contaminated water where it causes harm or breaches site rules.
Follow safety data sheets (COSHH), site procedures, and environmental requirements.
Refrigerant recovery is specialist F-Gas work.
Final Step: Record disposal method where required.
Notes: Tutor note:
Safe disposal is part of safe commissioning. Heating system water may contain chemicals, corrosion products, sludge or glycol. Refrigerant is not disposed of by a general installer; recovery/disposal must be by appropriately certified personnel.
Link to Water Regulations: protect wholesome water supply and prevent contamination/backflow when filling/connecting.

## Slide 20: Worked scenario: pressure test fails
Scenario
ASHP heating circuit is hydraulically pressure tested.
The Problem
Initial test pressure is reached, but pressure drops during the test period.
Possible Causes
• Leak or trapped air
• Temperature change
• Gauge or test hose issue
Resolution Steps
01. ACTION: Isolate sections, inspect joints/components and repair within competence
02. RETEST: Retest after correction and record final pass/fail evidence
03. ESCALATE: Escalate if fault involves regulated work or manufacturer support
Notes: Tutor guide:
Use this scenario to show evidence-based decision making. Learners should not simply 'top it up and carry on'.
Learner output: test record entry including initial pressure, final pressure, duration, area tested, findings, corrective action and retest result.

## Slide 21: Activity: choose the right testing technique
For each scenario, choose the most suitable testing/check method:
New radiator circuit before insulation is fitted
Suspected blocked strainer after commissioning fault
DHW not reaching required temperature
Customer reports noise after handover
ASHP condensate/defrost water pooling near walkway
Notes: Suggested approaches:
- New radiator circuit: soundness/hydraulic pressure test (or air test only if permitted/safe).
- Blocked strainer: operational flow/temperature checks + inspect/clean strainer.
- DHW temp issue: temperature testing, controls/DHW priority/sensor checks.
- Noise: pressure/flow/pump/balancing checks.
- Pooling: drainage/defrost water inspection and safe discharge route.
Workbook task created separately.

## Slide 22: Recap checkpoint
1
What are the stages of a soundness test?
2
Why can air testing be more hazardous than hydraulic testing?
3
Name four operational checks used during commissioning.
4
What should be recorded after a failed test?
5
Give one example of a testing by-product requiring safe disposal.
Notes: Suggested answers:
1) Initial fill, stabilise, test to required pressure, leak check, check pressure after test period, record.
2) Compressed air stores energy and failure can be violent.
3) Temperature, flow rate, pressure, controls.
4) Pressures, duration, area, fault, repair, retest, person responsible.
5) Chemical flush water, glycol/brine, dirty sludge water, refrigerant (specialist recovery).
Wordwall/Quizizz recap created separately.

## Slide 23: Summary and questions
Commissioning Focus
K1.40 focuses on how systems are tested during commissioning processes.
Soundness Testing
Soundness testing proves pipework and components hold pressure effectively.
Operational Checks
Checks prove temperature, flow, pressure and controls work as intended.
Safety & Performance
Testing must follow manufacturer instructions and stay within competence limits.
Records & Disposal
Safe disposal and clear records protect the customer, engineer, and environment.
Notes: Final prompt: ask learners to explain the difference between 'soundness testing' and 'performance testing' in one sentence.

## Slide 24
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.