## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.43: Causes of typical faults in low carbon heating and hot water systems

## Slide 2
Introduction / starter
Warm-up
When a low carbon system fails, is it always a failed component?
Pair-share
List three possible causes of a heat pump fault.
Tutor prompt
Faults usually come from installation, design, user operation, environment or component failure.
Notes: Stop point: 3–5 minute discussion. Draw out poor installation, inadequate design, user error, environmental factors, appliance/component malfunction, controls and water quality.

## Slide 3: Objectives (K1.43)
System Identification
Identify causes of common faults in low carbon heating and hot water systems.
Root Cause Analysis
Link symptoms to root causes: installation, design, user error, environment and malfunction.
Fault Recognition
Recognise typical wet system faults: leaks, noise, corrosion, blockages and low flow.
Technology Specifics
Explain typical heat pump (fuse, pressure, PCB) and solar thermal (glycol, leaks, vessel) faults.
Decision Making: Evidence-based Maintenance and Escalation
Use evidence to decide whether to maintain, repair, refer or escalate
Notes: Learners should understand root cause thinking. A fault symptom is not always the actual cause.

## Slide 4: Fault categories: root causes
1. Poor Installation
Workmanship or commissioning errors. Includes poor pipe layout, incorrect sizing, inadequate insulation, or improper flushing.
2. Inadequate Design
System fails to meet property demand. Includes incorrect heat loss calculations, undersized emitters, or poor zoning strategy.
3. User Operation
Operational issues due to customer misuse. Includes incorrect thermostat settings, frequent overrides, or closing too many TRVs.
4. Environmental Factors
External conditions affecting performance. Includes extreme low temperatures, restricted ASHP airflow, or poor source water quality.
5. Component Malfunction
Wear, contamination, or manufacturing defects in physical parts. Affects pumps, valves, sensors, compressors, or heat exchangers.
6. Electrical and Control Faults
Sensor calibration errors, communication failures, or wiring issues that can falsely mimic hydraulic or refrigeration faults.
System-Wide Perspective: Most faults involve multiple categories
Many breakdowns result from combinations (e.g. poor installation causes low flow, leading to a high-pressure trip misdiagnosed as compressor failure). Engineers must investigate the whole system.
Notes: Tutor note:
Use this slide as the framework for the whole lesson. Learners should ask: is the component faulty, or is the system making it look faulty?
Example: low-flow fault may be caused by blocked strainer, air, closed valve, pump issue, design issue or sensor issue.

## Slide 5: Poor installation: typical fault causes
1. Pipework Installation
Faults: Undersized pipes, excessive bends, incorrect layout, or poor insulation.
Impact: Heat loss, vibration, noise, and restricted flow rates.
2. Hydraulic Arrangement
Faults: Closed isolation valves, missing bypasses, or wrong pump settings.
Impact: Low-flow alarms, high pressure, and poor performance.
3. Cleaning and Treatment
Faults: Inadequate debris flushing, wrong inhibitor, or incorrect glycol dosing.
Impact: Sludge, blocked strainers, and premature pump wear.
4. Controls and Sensors
Faults: Incorrect sensor placement, wiring errors, or wrong configuration.
Impact: Poor weather compensation and inaccurate temperatures.
5. Outdoor Unit Siting
Faults: Restricted airflow, cold air recirculation, or blocked drainage.
Impact: Increased defrost frequency and reduced efficiency.
6. Commissioning and Docs
Faults: Incomplete records, unverified flow rates, or weak handover.
Impact: Delayed warranty claims and difficult troubleshooting.
Standards and Compliance: Installation must follow recognised codes
Low carbon systems must comply with manufacturer instructions, MCS MIS 3005, Building Regulations, and British Standards. Following recognised standards improves overall system reliability, protects product warranties, and reduces callbacks.
Notes: Tutor depth:
Poor installation can create faults immediately or months later. Examples: missing insulation on external ASHP pipework increases freeze/heat loss risk; poor clipping causes noise; unflushed pipework blocks strainers.
Reference in notes: MCS/NHBC best practice guide supports good design, installation and commissioning principles for domestic heat pumps.
Tutor Example
A newly installed monobloc ASHP repeatedly reports a low-flow fault shortly after handover.
The engineer discovers:
External pipework has not been insulated correctly.
A magnetic filter is blocked with installation debris because the system was not flushed adequately.
Several isolation valves have been left partially closed.
The circulation pump has been left on the factory default setting instead of being commissioned for the system.
Once the system is flushed, valves opened, pump settings adjusted and pipework insulation corrected, the fault is resolved without replacing any components.
Learning point: The heat pump itself was not faulty—the installation and commissioning process created the fault.
Learner Takeaway
The quality of the installation determines the quality of the system.
Many faults seen during the first few months of operation are installation-related rather than equipment failures. By following the manufacturer's instructions, complying with MCS, Building Regulations and relevant British Standards, correctly flushing and treating the system, commissioning it thoroughly and maintaining accurate records, installers can significantly improve system reliability, maximise efficiency, protect warranties and reduce unnecessary call-backs.

## Slide 6: Inadequate design: typical fault causes
2. Hydraulic and Volume
Flow restrictions and loop volume:
Poor Piping Layout: Restricting circulation causes high pressure drops, low-flow alarms, and repeated compressor protection trips.
Insufficient Water Volume: Small heating circuits or closed TRVs trigger rapid temperature swings and excessive compressor cycling.
3. DHW and Control Strategy
Hot water sizing and settings:
Incorrect DHW Design: Unsuitable cylinders with small coil heat exchangers slow down hot water recovery and lower total system efficiency.
Controls and Standards: Poor control settings override weather compensation. Design must strictly comply with MCS MIS 3005 and Building Regs.
1. Sizing and Heat Loss
Under/oversizing and emitter issues:
Incorrect Calculations: Inaccurate heat loss estimates result in under/oversizing, leading to cold rooms, long run times, and high-power usage.
Undersized Emitters: Lower flow temperatures require larger emitters. Incorrect sizing leads to occupant comfort complaints and reliance on backup heaters.
Notes: Tutor note:
Design faults often appear as performance complaints, repeated alarms or high bills rather than one obvious broken part.
Manufacturer example: Daikin installer guidance states that minimum flow rate must be guaranteed; if not, a 7H flow error may be generated. Use this as a tutor example only, not a generic code for all manufacturers.
Tutor Example
A property owner complains that their new 8 kW air source heat pump cannot maintain 21°C indoors during winter.
Inspection shows:
The heat pump is operating exactly as designed.
Flow and return temperatures are within specification.
No fault codes are present.
Further investigation reveals:
Several radiators are undersized for the design flow temperature.
The domestic hot water cylinder has a coil intended for a gas boiler rather than a heat pump.
No volumiser has been installed despite limited system water volume.
The heat pump itself is not faulty—the system design is preventing it from achieving the required performance.
Learner Takeaway
Good installation cannot overcome poor design.
Many recurring heat pump problems originate during the design stage, not during installation or maintenance. Correct heat loss calculations, emitter sizing, hydraulic design, hot water cylinder selection, system water volume and control strategy are essential for reliable, efficient operation. Before replacing components, always consider whether the system has been designed to allow the heat pump to operate as intended.

## Slide 7: User error and handover-related faults (slide 1 of 3)
1. User Misconceptions
Misusing basic temperature controls:
Thermostats: Turning to max or switching on/off does not heat faster; it increases cycling, reduces CoP, and lowers compressor life.
Heating Off vs. Set-back: Complete overnight shut-off forces long recovery times. Modest set-back temperatures maintain efficiency.
TRVs and Zoning: Closing too many radiator valves reduces flow rates, triggering low-flow alarms or short cycling.
Notes: Tutor depth:
User error is often a handover or communication issue. Avoid blaming language. Ask: did the customer receive clear instructions and understand low-temperature operation?
Link to K1.15 controls and K1.41 handover documents.
Tutor Example
A customer complains that their new air source heat pump is "too expensive to run“.
During the service visit, the engineer discovers:
The thermostat has been set to 28°C every morning.
The heating is turned off completely every night.
The immersion heater has been left permanently enabled.
Several TRVs are fully closed upstairs.
The outdoor unit is partially blocked by garden furniture.
No components are faulty.
After explaining how the heat pump is designed to operate, adjusting the controls, reopening the TRVs and restoring clear airflow, the system runs more efficiently and the customer's energy consumption reduces significantly.
Learning point: The heat pump was operating correctly—the issue was customer operation combined with an inadequate handover.
Learner Takeaway
A good handover is one of the most effective forms of fault prevention.
Many reported heat pump faults are actually operational issues rather than equipment failures. By explaining how low-temperature heating works, demonstrating the controls, advising on efficient operation and providing clear user documentation, installers can reduce unnecessary call-backs, improve customer satisfaction, maximise system efficiency and help maintain manufacturer warranty compliance.

## Slide 8: User error and handover-related faults (slide 2 of 3)
2. Controls and Settings
Misunderstanding automated systems:
Hot Water (DHW) Controls: Unnecessary manual use of 'DHW Boost' or immersion heaters significantly raises electric consumption.
Weather Compensation: Continually changing thermostat points overrides automated flow curve optimisation, lowering seasonal efficiency.
Smart Features: Incorrect scheduling, holiday mode mistakes, and failure to match smart controls to time-of-use tariffs hinder proper function.
Notes: Tutor depth:
User error is often a handover or communication issue. Avoid blaming language. Ask: did the customer receive clear instructions and understand low-temperature operation?
Link to K1.15 controls and K1.41 handover documents.
Tutor Example
A customer complains that their new air source heat pump is "too expensive to run“.
During the service visit, the engineer discovers:
The thermostat has been set to 28°C every morning.
The heating is turned off completely every night.
The immersion heater has been left permanently enabled.
Several TRVs are fully closed upstairs.
The outdoor unit is partially blocked by garden furniture.
No components are faulty.
After explaining how the heat pump is designed to operate, adjusting the controls, reopening the TRVs and restoring clear airflow, the system runs more efficiently and the customer's energy consumption reduces significantly.
Learning point: The heat pump was operating correctly—the issue was customer operation combined with an inadequate handover.
Learner Takeaway
A good handover is one of the most effective forms of fault prevention.
Many reported heat pump faults are actually operational issues rather than equipment failures. By explaining how low-temperature heating works, demonstrating the controls, advising on efficient operation and providing clear user documentation, installers can reduce unnecessary call-backs, improve customer satisfaction, maximise system efficiency and help maintain manufacturer warranty compliance.

## Slide 9: User error and handover-related faults (slide 3 of 3)
3. Maintenance and Handover
Ensuring lifetime performance:
Ignored Maintenance: Neglecting airflow clearance, debris clearing, or annual pressure and glycol checks degrades system life and can void warranties.
The Handover Process: Installers must demo the controller, explain schedules, highlight basic fault codes, and outline homeowner care duties.
Proactive Education: An informed customer is far less likely to report false errors or trigger operational service calls.
Notes: Tutor depth:
User error is often a handover or communication issue. Avoid blaming language. Ask: did the customer receive clear instructions and understand low-temperature operation?
Link to K1.15 controls and K1.41 handover documents.
Tutor Example
A customer complains that their new air source heat pump is "too expensive to run“.
During the service visit, the engineer discovers:
The thermostat has been set to 28°C every morning.
The heating is turned off completely every night.
The immersion heater has been left permanently enabled.
Several TRVs are fully closed upstairs.
The outdoor unit is partially blocked by garden furniture.
No components are faulty.
After explaining how the heat pump is designed to operate, adjusting the controls, reopening the TRVs and restoring clear airflow, the system runs more efficiently and the customer's energy consumption reduces significantly.
Learning point: The heat pump was operating correctly—the issue was customer operation combined with an inadequate handover.
Learner Takeaway
A good handover is one of the most effective forms of fault prevention.
Many reported heat pump faults are actually operational issues rather than equipment failures. By explaining how low-temperature heating works, demonstrating the controls, advising on efficient operation and providing clear user documentation, installers can reduce unnecessary call-backs, improve customer satisfaction, maximise system efficiency and help maintain manufacturer warranty compliance.

## Slide 10: Environmental factors (Slide 1 of 3)
1. Heat Pump Systems
ASHP, GSHP and WSHP hazards:
Air Source (ASHP): Debris, snow, ice, or wind-driven recirculation restricts airflow, increasing compressor run times and reducing CoP.
Ground Source (GSHP): Incorrect glycol levels, air pockets, or loop freezing degrades thermal conductivity and circulation.
Water Source (WSHP): Fouling of strainers, sediment buildup, and biological growth restrict source flow and trigger pressure faults.
Notes: Tutor note:
Environmental factors do not always mean the appliance is faulty. Example: ASHP defrost is normal, but poor condensate drainage can create ice and safety risks.
Stop point: ask learners to classify environmental vs. design vs. component causes.
Tutor Example
An 8 kW air source heat pump operates normally throughout autumn but repeatedly displays low-flow and defrost-related faults during winter.
The engineer finds:
Leaves blocking the outdoor evaporator.
A frozen condensate drain preventing correct defrost operation.
Damaged insulation on external pipework.
A partially blocked magnetic filter reducing water circulation.
No components have failed. After restoring airflow, clearing the condensate drain, replacing the insulation and cleaning the filter, the heat pump returns to normal operation.
Learning point: The environmental conditions did not cause the fault directly—they exposed weaknesses in maintenance and system performance.
Learner Takeaway
The environment is part of the heating system.
Low carbon heating technologies rely on air, ground, water or solar energy as their heat source. Changes in environmental conditions can significantly affect efficiency, heat output and reliability. Good engineers always consider weather, airflow, source conditions, water quality and seasonal effects alongside hydraulic, electrical and refrigerant diagnostics before identifying the root cause of a fault.

## Slide 11: Environmental factors (Slide 2 of 3)
2. Solar and Water Factors
Critical environmental risks:
Solar Thermal Gain: Shading, collector contamination (dirt, leaves), UV insulation decay, and stagnation degrade performance.
Water Quality: Poor water quality blocks filters, limits heat transfer, and accelerates wet system wear across all heat sources.
System Failures: Hard water, limescale, sludge, and magnetite buildup heavily increase pump workload and drop system efficiency.
Notes: Tutor note:
Environmental factors do not always mean the appliance is faulty. Example: ASHP defrost is normal, but poor condensate drainage can create ice and safety risks.
Stop point: ask learners to classify environmental vs. design vs. component causes.
Tutor Example
An 8 kW air source heat pump operates normally throughout autumn but repeatedly displays low-flow and defrost-related faults during winter.
The engineer finds:
Leaves blocking the outdoor evaporator.
A frozen condensate drain preventing correct defrost operation.
Damaged insulation on external pipework.
A partially blocked magnetic filter reducing water circulation.
No components have failed. After restoring airflow, clearing the condensate drain, replacing the insulation and cleaning the filter, the heat pump returns to normal operation.
Learning point: The environmental conditions did not cause the fault directly—they exposed weaknesses in maintenance and system performance.
Learner Takeaway
The environment is part of the heating system.
Low carbon heating technologies rely on air, ground, water or solar energy as their heat source. Changes in environmental conditions can significantly affect efficiency, heat output and reliability. Good engineers always consider weather, airflow, source conditions, water quality and seasonal effects alongside hydraulic, electrical and refrigerant diagnostics before identifying the root cause of a fault.

## Slide 12: Environmental factors (Slide 3 of 3)
3. Design and Maintenance
Mitigation and resilience:
Exposing Weaknesses: Extreme winter weather exposes underlying faults in system design, building insulation, or commissioning margins.
Proactive Servicing: Inspecting outdoor clearances, condensate drains, insulation, and system chemistry prevents severe cold-weather dropouts.
Long-term Life: Regular maintenance sustains high CoP, reduces electrical wear, and prevents costly winter component breakdowns.
Notes: Tutor note:
Environmental factors do not always mean the appliance is faulty. Example: ASHP defrost is normal, but poor condensate drainage can create ice and safety risks.
Stop point: ask learners to classify environmental vs. design vs. component causes.
Tutor Example
An 8 kW air source heat pump operates normally throughout autumn but repeatedly displays low-flow and defrost-related faults during winter.
The engineer finds:
Leaves blocking the outdoor evaporator.
A frozen condensate drain preventing correct defrost operation.
Damaged insulation on external pipework.
A partially blocked magnetic filter reducing water circulation.
No components have failed. After restoring airflow, clearing the condensate drain, replacing the insulation and cleaning the filter, the heat pump returns to normal operation.
Learning point: The environmental conditions did not cause the fault directly—they exposed weaknesses in maintenance and system performance.
Learner Takeaway
The environment is part of the heating system.
Low carbon heating technologies rely on air, ground, water or solar energy as their heat source. Changes in environmental conditions can significantly affect efficiency, heat output and reliability. Good engineers always consider weather, airflow, source conditions, water quality and seasonal effects alongside hydraulic, electrical and refrigerant diagnostics before identifying the root cause of a fault.

## Slide 13: Appliance/component malfunction (Slide 1 of 3)
1. Root Cause and Failures
Diagnosing beyond symptoms:
Secondary Faults: Many component failures are secondary faults where another system issue (sludge, poor flow, air) caused the failure.
Common Culprits: Circulation pumps, motorised/diverter valves, sensors, PCBs, compressors, and expansion vessels.
Root Cause Rule: Good fault-finding identifies the underlying cause before replacement, preventing repeat failure.
Notes: Tutor depth:
A component may fail because of age, but also because the system conditions are wrong. Example: repeated pump failure may be caused by sludge/debris or cavitation.
Link to K1.44: structured diagnosis before replacement.
Tutor Example
A customer reports repeated high-pressure faults on their air source heat pump. The engineer initially suspects the circulation pump has failed.
Following a structured diagnosis, they discover:
The pump is operating correctly.
The magnetic filter is heavily blocked with magnetite.
Water flow through the condenser is significantly below the manufacturer's minimum requirement.
The restricted flow is causing the refrigerant pressure to rise, triggering the safety protection.
After cleaning the filter, restoring the correct flow rate and retesting, the fault is resolved without replacing any components.
Learning point: The pump was not the failed component—it was operating in poor system conditions created by contaminated water.
Learner Takeaway
A failed component is not always the root cause of the fault.
Professional fault-finding means understanding why a component has failed before replacing it. By combining manufacturer diagnostics, operating data, water quality checks, hydraulic assessment and electrical testing (within competence), engineers can avoid unnecessary repairs, improve first-time fix rates, protect manufacturer warranties and significantly reduce repeat call-backs.

## Slide 14: Appliance/component malfunction (Slide 2 of 3)
2. Diagnostics and Pressure
Tools and critical inspection:
Smart Diagnostics: Utilise fault codes, live operating data, and alarm history, but remember: codes identify systems, not just parts.
System Pressure: Expansion vessels (losing pre-charge/diaphragms) and pressure relief valves require careful checks.
Comprehensive Tests: Pair electronic diagnostics with temperature, pressure, flowrate, and electrical testing.
Notes: Tutor depth:
A component may fail because of age, but also because the system conditions are wrong. Example: repeated pump failure may be caused by sludge/debris or cavitation.
Link to K1.44: structured diagnosis before replacement.
Tutor Example
A customer reports repeated high-pressure faults on their air source heat pump. The engineer initially suspects the circulation pump has failed.
Following a structured diagnosis, they discover:
The pump is operating correctly.
The magnetic filter is heavily blocked with magnetite.
Water flow through the condenser is significantly below the manufacturer's minimum requirement.
The restricted flow is causing the refrigerant pressure to rise, triggering the safety protection.
After cleaning the filter, restoring the correct flow rate and retesting, the fault is resolved without replacing any components.
Learning point: The pump was not the failed component—it was operating in poor system conditions created by contaminated water.
Learner Takeaway
A failed component is not always the root cause of the fault.
Professional fault-finding means understanding why a component has failed before replacing it. By combining manufacturer diagnostics, operating data, water quality checks, hydraulic assessment and electrical testing (within competence), engineers can avoid unnecessary repairs, improve first-time fix rates, protect manufacturer warranties and significantly reduce repeat call-backs.

## Slide 15: Appliance/component malfunction (Slide 3 of 3)
3. Warranty and Records
Evidence-based compliance:
Warranty Protection: Manufacturers require evidence (commissioning logs, water quality tests, glycol concentration) to approve parts.
Document Everything: Record symptoms, fault codes, operating conditions, diagnostic steps, and final post-repair readings.
Professional Standard: Accurate evidence supports warranty claims and demonstrates professional, systematic diagnosis.
Notes: Tutor depth:
A component may fail because of age, but also because the system conditions are wrong. Example: repeated pump failure may be caused by sludge/debris or cavitation.
Link to K1.44: structured diagnosis before replacement.
Tutor Example
A customer reports repeated high-pressure faults on their air source heat pump. The engineer initially suspects the circulation pump has failed.
Following a structured diagnosis, they discover:
The pump is operating correctly.
The magnetic filter is heavily blocked with magnetite.
Water flow through the condenser is significantly below the manufacturer's minimum requirement.
The restricted flow is causing the refrigerant pressure to rise, triggering the safety protection.
After cleaning the filter, restoring the correct flow rate and retesting, the fault is resolved without replacing any components.
Learning point: The pump was not the failed component—it was operating in poor system conditions created by contaminated water.
Learner Takeaway
A failed component is not always the root cause of the fault.
Professional fault-finding means understanding why a component has failed before replacing it. By combining manufacturer diagnostics, operating data, water quality checks, hydraulic assessment and electrical testing (within competence), engineers can avoid unnecessary repairs, improve first-time fix rates, protect manufacturer warranties and significantly reduce repeat call-backs.

## Slide 16: Wet system faults: leaks, noise and corrosion
1. Leaks and Pressure
Safety, causes and impact:
System Impact: Reduces pressure, introduces fresh oxygen, and severely degrades heat transfer efficiency.
Key Causes: Poorly installed joints, failed seals, frozen pipework, and expansion vessel or PRV faults.
Consequences: Even minor, ignored leaks trigger repeated pressure loss, sludge, and premature failure.
2. Noise and Vibration
Acoustic clues and support:
Diagnostic Clues: Unusual noise always warrants investigation. Location helps pinpoint the exact fault.
Common Sources: Trapped air, pump cavitation, excessive velocity, loose pipework, or thermal expansion.
Support/Clipping: Poorly supported pipes cause stress on joints, transfer vibration, and lead to fatigue.
3. Corrosion and Mitigation
Water quality and inspection:
System Degradation: Oxygen ingress, depleted inhibitors, and incompatible mixed metals accelerate sludge.
Insulation and Flow: Damaged insulation causes heat loss, condensation on chilled lines, and freezing risk.
Best Practice: Flushing systems, checking water quality, and keeping detailed pressure/photo logs.
Notes: Tutor note:
Noise is a symptom, not a diagnosis. Learners should identify the source: pump, fan, pipe movement, air, valve chatter or water hammer.
Water quality link: BS 7593 principles may be relevant to preparation/maintenance of domestic heating/cooling water systems.
Tutor Example
A customer reports that their heat pump has needed topping up several times over the past few months and has become noticeably noisier.
During inspection, the engineer finds:
A small leak on a compression fitting.
Low system pressure.
Air trapped in several upstairs radiators.
Corrosion beginning around the leaking joint.
Missing insulation on external flow and return pipework.
After repairing the leak, restoring the correct pressure, venting the system, replacing the insulation and checking inhibitor levels, the heating system operates quietly and pressure remains stable.
Learning point: A seemingly minor leak can create multiple secondary faults, including air ingress, corrosion, poor circulation, reduced efficiency and increased running costs.
Learner Takeaway
Water is the heat transfer medium in every wet low carbon heating system—keeping it contained, clean and circulating correctly is essential.
Many faults that appear to be heat pump problems are actually wet system faults. Early identification of leaks, noise, corrosion, poor pipe support and damaged insulation can prevent expensive component failures, improve system efficiency, protect manufacturer warranties and significantly extend the life of the heating system.

## Slide 17: Flow and blockage-related faults (Slide 1 of 3)
1. Flow and Blockages
Flow constraints and blockages:
Critical Flow: Continuous flow is vital. Restrictions reduce CoP/SCoP and trigger low-flow or high-pressure alarms.
Blockage Causes: Gradual build-up of sludge/magnetite, installation debris, scale, air locks, or blocked filters and strainers.
System Impact: Causes excessive ΔT, low-flow fault codes, high-pressure trips, and increased compressor cycling.
Notes: Tutor depth:
Low carbon systems need stable flow. A small restriction can cause multiple symptoms. Discuss how blocked filters can make the heat pump appear faulty.
Manufacturer example in notes: Daikin 7H flow error can occur if minimum water flow is not guaranteed in all conditions.
Tutor Example
A 10 kW air source heat pump repeatedly displays a low-flow alarm, particularly during domestic hot water production.
The engineer initially suspects a circulation pump fault. However, a structured investigation identifies:
A heavily blocked magnetic filter.
Two TRVs closed upstairs.
A flow/return temperature difference of 18°C, significantly above the manufacturer's design value.
Reduced flow through the heat pump.
After cleaning the filter, reopening the TRVs, rebalancing the heating circuit and confirming the correct flow rate, the ΔT returns to approximately 5–7°C, the fault clears and the heat pump operates normally.
Learning point: The circulation pump was operating correctly—the restriction within the hydraulic circuit was preventing the heat pump from transferring heat efficiently.
Learner Takeaway
For a heat pump, good water flow is just as important as the refrigeration cycle.
Many heat pump faults—including low-flow alarms, high-pressure trips, poor domestic hot water recovery, high running costs and uneven heating—can be traced back to restrictions within the hydraulic circuit. Before replacing expensive components, always check the flow rate, system pressure, filters, strainers, balancing, valves and water quality, following the manufacturer's commissioning data and fault-finding procedures.

## Slide 18: Flow and blockage-related faults (Slide 2 of 3)
2. Distribution and Venting
Circulation and air issues:
Cold Emitters: Cold areas in radiators or underfloor circuits indicate trapped air, sludge restriction, or poor hydraulic balancing.
Venting and Leaks: Repeated bleeding is abnormal. Indicates air ingress through vents/joints, system leaks, or expansion vessel faults.
Corrosion Risk: Continual manual topping up introduces fresh oxygen, rapidly accelerating corrosion and sludge formation.
Notes: Tutor depth:
Low carbon systems need stable flow. A small restriction can cause multiple symptoms. Discuss how blocked filters can make the heat pump appear faulty.
Manufacturer example in notes: Daikin 7H flow error can occur if minimum water flow is not guaranteed in all conditions.
Tutor Example
A 10 kW air source heat pump repeatedly displays a low-flow alarm, particularly during domestic hot water production.
The engineer initially suspects a circulation pump fault. However, a structured investigation identifies:
A heavily blocked magnetic filter.
Two TRVs closed upstairs.
A flow/return temperature difference of 18°C, significantly above the manufacturer's design value.
Reduced flow through the heat pump.
After cleaning the filter, reopening the TRVs, rebalancing the heating circuit and confirming the correct flow rate, the ΔT returns to approximately 5–7°C, the fault clears and the heat pump operates normally.
Learning point: The circulation pump was operating correctly—the restriction within the hydraulic circuit was preventing the heat pump from transferring heat efficiently.
Learner Takeaway
For a heat pump, good water flow is just as important as the refrigeration cycle.
Many heat pump faults—including low-flow alarms, high-pressure trips, poor domestic hot water recovery, high running costs and uneven heating—can be traced back to restrictions within the hydraulic circuit. Before replacing expensive components, always check the flow rate, system pressure, filters, strainers, balancing, valves and water quality, following the manufacturer's commissioning data and fault-finding procedures.

## Slide 19: Flow and blockage-related faults (Slide 3 of 3)
3. Hydraulics and Diagnosis
Evidence-based troubleshooting:
Hydraulic Stability: Low-carbon systems depend on correct balancing, system pressure, clean filters, and adequate water volume.
Record Evidence: Always record flow/return temperatures (ΔT), pressure, flow rates, and filter condition before component replacement.
Verification: Compare field diagnostic readings against the manufacturer's design data and commissioning logs first.
Notes: Tutor depth:
Low carbon systems need stable flow. A small restriction can cause multiple symptoms. Discuss how blocked filters can make the heat pump appear faulty.
Manufacturer example in notes: Daikin 7H flow error can occur if minimum water flow is not guaranteed in all conditions.
Tutor Example
A 10 kW air source heat pump repeatedly displays a low-flow alarm, particularly during domestic hot water production.
The engineer initially suspects a circulation pump fault. However, a structured investigation identifies:
A heavily blocked magnetic filter.
Two TRVs closed upstairs.
A flow/return temperature difference of 18°C, significantly above the manufacturer's design value.
Reduced flow through the heat pump.
After cleaning the filter, reopening the TRVs, rebalancing the heating circuit and confirming the correct flow rate, the ΔT returns to approximately 5–7°C, the fault clears and the heat pump operates normally.
Learning point: The circulation pump was operating correctly—the restriction within the hydraulic circuit was preventing the heat pump from transferring heat efficiently.
Learner Takeaway
For a heat pump, good water flow is just as important as the refrigeration cycle.
Many heat pump faults—including low-flow alarms, high-pressure trips, poor domestic hot water recovery, high running costs and uneven heating—can be traced back to restrictions within the hydraulic circuit. Before replacing expensive components, always check the flow rate, system pressure, filters, strainers, balancing, valves and water quality, following the manufacturer's commissioning data and fault-finding procedures.

## Slide 20: Pressure, discharge and backflow issues (Slide 1 of 3)
1. Valves and Flow Controls
System impact and typical faults:
TRV Issues: Stuck, seized, or incorrectly adjusted TRVs restrict water circulation, resulting in low-flow alarms, excessive cycling, and cold radiators.
Motorised Valves: Faulty two-port, three-port, or diverter valves can prevent heating/DHW operation, cause unwanted heat, or restrict system flow.
Flow Routes: Always check that any minimum flow route or bypass arrangement remains available to ensure sufficient system flow.
Notes: Tutor note:
Keep Water Regulations at awareness level. Heating system water may contain inhibitor/glycol and is not wholesome. Incorrect backflow protection can create contamination risk. Ask learners: why is the fluid category important?
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 21: Pressure, discharge and backflow issues (Slide 2 of 3)
2. Electronic Controls and Comms
System coordination and faults:
Control Failures: Faults in thermostats, programmers, or PCBs can significantly reduce overall system performance without any physical components actually failing.
Comms and Sensors: Interrupted communication or incorrect sensor readings cause poor weather compensation, false fault codes, and unnecessary cycling.
Commissioning: Incorrect settings or improper controller commissioning will severely degrade low-carbon system efficiency.
Notes: Tutor note:
Keep Water Regulations at awareness level. Heating system water may contain inhibitor/glycol and is not wholesome. Incorrect backflow protection can create contamination risk. Ask learners: why is the fluid category important?
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 22: Pressure, discharge and backflow issues (Slide 3 of 3)
3. Electrical Protection and Safety
Protocols and diagnosis:
Electrical Protection: Blown fuses or tripped MCBs indicate short circuits, earth faults, moisture ingress, or loose terminals rather than a simple fuse fault.
Safe Isolation: Electrical inspection and testing must strictly follow safe isolation procedures and be carried out only by competent, qualified persons.
Diagnosis: Compare electrical and sensor readings with the manufacturer's service manual. Always record fault codes and corrective actions taken.
Notes: Tutor note:
Keep Water Regulations at awareness level. Heating system water may contain inhibitor/glycol and is not wholesome. Incorrect backflow protection can create contamination risk. Ask learners: why is the fluid category important?
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 23: Controls and electrical/electronic faults (Slide 1 of 3)
1. Valves and Flow Control
TRVs and Motorised Valves:
TRV Issues: Stuck or incorrectly adjusted TRVs restrict water flow, causing low-flow alarms, excessive cycling, and reduced system efficiency.
Motorised Valves: Faulty 2/3-port or diverter valves can block heating/DHW, cause heating when there is no demand, or trigger fault codes.
Flow Routes: Always check that any minimum flow route or bypass arrangement remains available.
Notes: Tutor depth:
Control faults often mimic heat pump faults. Example: no heating could be schedule, zone valve, thermostat, controller, pump, flow or appliance fault.
Link to K1.15 controls and K1.44 multimeter testing competence boundaries.
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 24: Controls and electrical/electronic faults (Slide 2 of 3)
2. Controls, Comms and Electrical
Wiring, Sensors and Protection:
Control Failures: Faults in controllers, programmers, wiring centres, or PCBs can degrade performance without any component actually failing.
Comms and Sensors: Communication losses and faulty sensors lead to wrong weather compensation, poor DHW, and false fault codes.
Electrical Protection: Blown fuses or tripped MCBs point to underlying issues like short circuits, earth faults, or moisture ingress.
Notes: Tutor depth:
Control faults often mimic heat pump faults. Example: no heating could be schedule, zone valve, thermostat, controller, pump, flow or appliance fault.
Link to K1.15 controls and K1.44 multimeter testing competence boundaries.
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 25: Controls and electrical/electronic faults (Slide 3 of 3)
3. Unwanted Heat and Safe Diagnosis
System checks and safety protocols:
Unwanted Heating: Compare controller mode with actual system behaviour before replacing parts. Often caused by incorrect wiring or failed relays.
Safe Isolation: Electrical inspection and testing must strictly follow safe isolation procedures and be carried out only by competent persons.
Evidence Recording: Always record fault codes, electrical test results, controller settings, and corrective actions taken.
Notes: Tutor depth:
Control faults often mimic heat pump faults. Example: no heating could be schedule, zone valve, thermostat, controller, pump, flow or appliance fault.
Link to K1.15 controls and K1.44 multimeter testing competence boundaries.
Tutor Example
A customer reports that the house continues heating even though the thermostat is turned off.
The engineer initially suspects a controller fault but follows a structured diagnosis:
Confirms there is no heating demand at the controller.
Finds the two-port motorised valve remains mechanically open.
The circulation pump continues to circulate water through the heating circuit.
The actuator is replaced and the system retested.
Learning point: The heat pump was operating correctly—the fault was a stuck motorised valve, not the controller.
Learner Takeaway
Control faults can easily be mistaken for hydraulic or refrigeration faults.
Always compare what the controller is asking the system to do with what the system is actually doing. A structured diagnosis—checking controls, valves, sensors, wiring and electrical protection devices before replacing components—will improve first-time fix rates, reduce unnecessary costs and help maintain manufacturer warranty compliance.

## Slide 26: Expansion vessel and antifreeze/glycol faults
1. Expansion Vessel and Pressure
System impact and typical faults:
System Role: Accommodates fluid expansion to maintain stable operating pressure.
Common Faults: Loss of pre-charge, ruptured diaphragm, incorrect sizing, or closed valves.
Symptoms: Extreme pressure spikes when hot, drops when cold, and frequent PRV discharges.
2. Glycol Role and Concentration
Protection vs. performance:
Application: Protects GSHP brine circuits, monobloc ASHP external pipes, and solar thermal.
Under-concentration: Reduced frost protection risks frozen pipework and ruptured heat exchangers.
Over-concentration: Increases viscosity and pump load while reducing heat transfer and system CoP.
3. Glycol Condition and Testing
Evidence-based maintenance:
Degradation: Over time, glycol degrades, turns acidic, and forms sludge that blocks strainers and pumps.
Refractometer Testing: Check concentration levels and compare against manufacturer specs.
Best Practice: Record freeze protection, fluid condition, and trends to prevent repeat system breakdowns.
Notes: Tutor note:
Glycol is not 'more is always better'. Correct concentration balances frost protection, viscosity, pumping energy and heat transfer.
Link to K1.44 refractometer testing.
Tutor Example
A customer reports that their ASHP displays a high-pressure fault during domestic hot water production.
Although the fault code suggests a refrigeration issue, the engineer first checks the hydraulic circuit and discovers:
A blocked magnetic filter.
Reduced water flow through the condenser.
An excessive flow/return temperature difference.
After restoring the correct flow, the high-pressure fault disappears without replacing any refrigerant components.
Learning point: The symptom occurred in the refrigeration system, but the root cause was within the hydraulic circuit.
Learner Takeaway
Heat pump faults should never be viewed in isolation.
Every diagnosis should consider five key areas:
Electrical faults
Hydraulic (water-side) faults
Refrigeration circuit faults
Electronic controls
Sensors
Following this structured approach, together with the manufacturer's fault-finding procedures, will reduce unnecessary component replacement, improve first-time fix rates and protect manufacturer warranties.

## Slide 27: Heat pump faults: overview
1. Hydraulics and Sensors
Water-side issues and monitoring:
Hydraulic Faults: Low pressure, trapped air, blocked strainers, incorrect pump settings, or inadequate flow rate.
Sensors: Faults in outdoor air, flow/return, or pressure sensors provide incorrect data, leading to poor efficiency or shutdowns.
Can lead to reduced efficiency, poor heating, and high-pressure or low-flow alarms.
2. Electrical and Controls
Power, PCB, and communication:
Electrical Faults: Blown fuses, loose wiring, failed relays, or water ingress may prevent operation or cause shutdowns.
PCB and Electronics: Coordinate system hubs. Common issues include unit communication errors, failed PCBs, or software bugs.
3. Refrigeration and Diagnosis
F-Gas circuits and systematic analysis:
Refrigerant Circuit: Must be worked on by F-Gas engineers. Leaks, low charge, LP/HP trips, or compressor faults.
Interconnected Faults: Faults in one area produce symptoms elsewhere. Always verify root causes before replacing components.
System Guidance: Follow manufacturer manuals alongside live operating data and fault history records.
Notes: Tutor note:
Do not teach refrigerant repair procedure. Refrigerant faults must be referred to F-Gas qualified persons/manufacturer support.
Manufacturer examples in notes: Mitsubishi service information includes pressure sensor anomaly and pressure-related faults; always check the exact model service handbook.

## Slide 28: Heat pump electrical faults: fuse, PCB and controls
1. Fuses and Electrical Causes
Symptom vs. Root Cause:
A blown fuse is a symptom. Determine why the device operated before restoring power.
Common Causes:
Short circuits, water ingress, damaged cables, or loose terminals.
2. PCB Center and Diagnostics
System Hub:
The PCB monitors sensors, compressor, pumps, and safety systems.
Best Practice:
Always eliminate sensor, wiring, and power supply faults before replacing a costly PCB.
3. Control and Communication
Coordination:
Electronic controls coordinate heating, domestic hot water, and defrost cycles.
Common Faults:
Incorrect configuration, software bugs, or failed communication cables.
4. Safe Isolation and Testing
Safety Protocol:
Electrical testing must only be carried out by competent, trained personnel.
Mandatory Step:
Always follow safe isolation procedures before removing system covers.
Notes: Tutor depth:
A blown fuse should not simply be replaced repeatedly. Identify why it blew. Electrical diagnosis must be within competence.
Prompt: what evidence would you need before replacing a circuit board?
Tutor Example
An ASHP repeatedly blows its control circuit fuse.
Instead of simply fitting another fuse, the engineer follows a structured diagnostic process:
Carries out safe isolation.
Inspects wiring for damage.
Tests the circulation pump and actuator.
Finds water ingress into an external junction box causing a short circuit.
Repairs the wiring, replaces the damaged components, fits a new fuse and retests the system.
The PCB was never faulty—the protective device operated correctly to prevent further damage.
Learner Takeaway
Electrical faults should never be diagnosed by replacing parts until the fault disappears.
Always follow a structured evidence-based process: inspect, isolate safely, test, compare with manufacturer data, record your findings and only replace components once the root cause has been confirmed. This approach reduces repeat call-backs, protects manufacturer warranties and avoids unnecessary replacement of expensive components such as PCBs.

## Slide 29: Heat pump pressure trips: low and high pressure
Low-Pressure Trips (LP)
Indicates refrigerant pressure has fallen below the safe limit. Does not always mean a leak.
Common Causes:
Refrigerant leak / low charge
Low source temperature
Restricted evaporator airflow
Ice build-up / poor defrost
Reduced water or brine flow
Key Symptoms:
Reduced heating output
Excessive compressor run times
Icing of the evaporator coil
High-Pressure Trips (HP)
Occurs when refrigerant pressure rises above the safe limit, typically due to poor heat rejection.
Common Causes:
Low water flow through condenser
Blocked strainers / heat exchanger
Air trapped in the heating system
Closed valves / wrong pump settings
Overcharged refrigerant charge
Key Symptoms:
Immediate compressor shutdown
Abnormally high flow temperatures
Noisy or heavy operation
Notes: Tutor note:
Pressure trips are often protection actions. They protect the compressor/system. Do not bypass protection. Always follow manufacturer fault tree.
Use manufacturer service data as example only and stress model-specific documentation.
Tutor Example
A 12 kW ASHP repeatedly displays a high-pressure fault during domestic hot water production.
Instead of immediately assuming a refrigerant problem, the engineer follows a structured diagnosis:
System pressure is correct.
Magnetic filter is heavily contaminated.
Flow rate is below the manufacturer's minimum requirement.
The circulation pump is operating correctly.
The outdoor fan is operating normally.
After cleaning the magnetic filter and restoring the correct flow rate, the system completes the DHW cycle without another high-pressure trip.
Learning point: The refrigeration system was operating correctly—the hydraulic circuit prevented the heat from leaving the condenser, causing refrigerant pressure to rise.
Learner Takeaway
Low-pressure and high-pressure trips are protection faults, not component diagnoses.
Always investigate the water circuit, airflow or source-side conditions first, follow the manufacturer's diagnostic procedure, record the evidence, and only refer to an F-Gas certified engineer when the evidence indicates a fault within the sealed refrigerant circuit. This structured approach prevents unnecessary component replacement and protects both the system and the manufacturer's warranty.

## Slide 30: Heat pump pressure trips: low and high pressure
Investigate Hydraulics First
Most pressure trips are caused by water circulation issues, NOT refrigerant faults!
Essential Pre-Checklist:
System flow and pressure: Ensure adequate flow rates.
Temperature split (ΔT): Check flow and return.
Air and blockages: Bleed air and check magnetic filters.
Valves and pumps: Ensure isolation valves are fully open.
Rule of thumb: Always rule out water circulation issues before calling an F-Gas engineer.
Notes: Tutor note:
Pressure trips are often protection actions. They protect the compressor/system. Do not bypass protection. Always follow manufacturer fault tree.
Use manufacturer service data as example only and stress model-specific documentation.
Tutor Example
A 12 kW ASHP repeatedly displays a high-pressure fault during domestic hot water production.
Instead of immediately assuming a refrigerant problem, the engineer follows a structured diagnosis:
System pressure is correct.
Magnetic filter is heavily contaminated.
Flow rate is below the manufacturer's minimum requirement.
The circulation pump is operating correctly.
The outdoor fan is operating normally.
After cleaning the magnetic filter and restoring the correct flow rate, the system completes the DHW cycle without another high-pressure trip.
Learning point: The refrigeration system was operating correctly—the hydraulic circuit prevented the heat from leaving the condenser, causing refrigerant pressure to rise.
Learner Takeaway
Low-pressure and high-pressure trips are protection faults, not component diagnoses.
Always investigate the water circuit, airflow or source-side conditions first, follow the manufacturer's diagnostic procedure, record the evidence, and only refer to an F-Gas certified engineer when the evidence indicates a fault within the sealed refrigerant circuit. This structured approach prevents unnecessary component replacement and protects both the system and the manufacturer's warranty.

## Slide 31: Refrigerant leaks and sensor faults (Slide 1 of 2)
1. Refrigerant Leaks and Performance
Symptoms:
Reduced capacity, longer run times, poor CoP, evaporator icing, repeated low-pressure trips, and increased electricity consumption.
Causes:
Poor installation, damaged pipework, vibration, corrosion, failed joints, or loose connections.
2. Regulation and Pressure Trips
F-Gas Regulations:
The refrigerant circuit is sealed. Any leak detection, recovery, charging, or repair must only be performed by F-Gas certified personnel.
Pressure Trips:
Do not assume refrigerant charge is low. First eliminate water flow issues, blocked strainers, poor airflow, or pump faults.
Notes: Tutor depth:
Refrigerant leak diagnosis is not for unqualified persons. Learners should recognise signs and referral requirements.
Sensor example: a cylinder sensor positioned poorly may cause poor DHW recovery without the heat pump being faulty.

## Slide 32: Refrigerant leaks and sensor faults (Slide 2 of 2)
3. Sensor Faults and Impact
Controller Role:
Numerous sensors (outdoor air, flow, return, cylinder, refrigerant temp/pressure) monitor and control compressor and defrost cycles.
Impact of Faults:
Faulty sensors mislead the controller, resulting in poor efficiency, nuisance fault codes, or unnecessary compressor shutdowns.
4. Diagnosis and Evidence
External Causes:
Incorrect readings can stem from damaged wiring, loose connectors, moisture ingress, or poor sensor positioning rather than a failed sensor.
Best Practice:
Compare live operating data with manufacturer charts before replacing components. Record fault codes and electrical test results.
Notes: Tutor depth:
Refrigerant leak diagnosis is not for unqualified persons. Learners should recognise signs and referral requirements.
Sensor example: a cylinder sensor positioned poorly may cause poor DHW recovery without the heat pump being faulty.

## Slide 33: Source-side and technology-specific faults (Slide 1 of 2)
1. Air Source (ASHP)
Operation: Relies on unrestricted outdoor airflow. Faults: Blocked airflow (leaves/debris/ice), poor siting/clearance. Symptoms: Low capacity, high pressure trips, reduced CoP.
2. Ground Source (GSHP)
Operation: Depends on stable ground loop heat absorption. Faults: Loss of brine pressure, air in loop, poor purging/commissioning. Symptoms: Low flow alarms, freezing risk, reduced temperatures.
3. Water Source (WSHP)
Operation: Requires consistent water source and quality. Faults: Blocked strainers, biological fouling, scaling, chemistry limits. Symptoms: Poor heat transfer, pressure faults, reduced flow.
Notes: Tutor note:
This slide broadens low carbon awareness beyond ASHP. Ask learners to identify which faults are environmental/source-side and which are controls/design issues.
Tutor Example
An air source heat pump repeatedly reports a high-pressure fault during cold weather.
The compressor, sensors and controls all test correctly. However, inspection of the outdoor unit finds the evaporator almost completely blocked with leaves and ice, while the condensate drain has frozen, preventing effective defrost.
Once the airflow is restored, the drain cleared and the unit retested, the fault no longer occurs.
Learning point: The heat pump itself was not faulty—the source side was preventing the refrigeration cycle from operating efficiently.
Learner Takeaway
For all low carbon technologies, the heat source is just as important as the heat pump itself. A restriction in airflow, water flow or ground-loop circulation can reduce efficiency, increase running costs and generate fault codes, even when the heat pump and its components are operating correctly. Always diagnose the source side first before replacing expensive components.

## Slide 34: Source-side and technology-specific faults (Slide 2 of 2)
4. Exhaust Air (EAHP)
Operation: Recovers heat from mechanical extract ventilation. Faults: Blocked filters/grilles, dirty ductwork, fan failure. Symptoms: Poor DHW recovery, high fan noise, controller alarms.
5. Hybrid and Bi-valent Systems
Operation: Integrates heat pump with boiler or auxiliary heater. Faults: Incorrect changeover settings, poor control logic, sensor faults. Guidance: Refer combustion issues to Gas Safe / OFTEC engineers.
6. Diagnostics and Compliance
Analysis: Check flow, temps, pumps, and filters before part replacement. Service: Always follow manufacturer service manuals and fault-finding. Safety: Qualified personnel must handle refrigerant and electrical tasks.
Notes: Tutor note:
This slide broadens low carbon awareness beyond ASHP. Ask learners to identify which faults are environmental/source-side and which are controls/design issues.
Tutor Example
An air source heat pump repeatedly reports a high-pressure fault during cold weather.
The compressor, sensors and controls all test correctly. However, inspection of the outdoor unit finds the evaporator almost completely blocked with leaves and ice, while the condensate drain has frozen, preventing effective defrost.
Once the airflow is restored, the drain cleared and the unit retested, the fault no longer occurs.
Learning point: The heat pump itself was not faulty—the source side was preventing the refrigeration cycle from operating efficiently.
Learner Takeaway
For all low carbon technologies, the heat source is just as important as the heat pump itself. A restriction in airflow, water flow or ground-loop circulation can reduce efficiency, increase running costs and generate fault codes, even when the heat pump and its components are operating correctly. Always diagnose the source side first before replacing expensive components.

## Slide 35: Solar thermal faults: overview (Slide 1 of 3)
1. System and Fluid Essentials
Controlled Heat Transfer
Roof- or ground-mounted collectors absorb solar heat and transfer it to a cylinder using insulated pipework, pumps, and controllers.
Critical Heat Transfer Fluid
Specialist antifreeze/glycol fluid protects the system from freezing while carrying heat from collectors to the cylinder.
Fluid Degradation Risks
If fluid is degraded, contaminated, or has an incorrect mixture, the system loses efficiency, suffers poor circulation, or blocks.
Notes: Tutor depth:
Solar thermal systems can reach high temperatures. Maintenance issues may include degraded glycol, failed vessel, pump issues, air and stagnation. Work must follow manufacturer instructions and competence boundaries.
Reference in notes: Decerna discusses pressurisation and expansion vessel/glycol-related maintenance risks in solar thermal systems.
Tutor example
A customer reports that the solar thermal system is not helping to heat the hot water cylinder. On inspection, the controller shows a high collector temperature, but the cylinder temperature is not rising. This suggests that heat is available at the collectors, but it is not being transferred effectively.
Possible causes include a failed pump, air lock, blocked strainer, loss of pressure, degraded glycol, faulty sensor, failed expansion vessel or incorrect controller setting. The engineer should check system pressure, pump operation, flow, controller readings, glycol condition and fault history before replacing parts.
Learner takeaway
Solar thermal faults usually come down to three key questions: Is there enough pressure? Is the fluid able to flow? Is the heat transfer fluid in good condition?

## Slide 36: Solar thermal faults: overview (Slide 2 of 3)
2. Typical Faults and Symptoms
Common System Faults
Typical issues include leaks, blockages, pump/sensor failure, loss of pressure, expansion vessel faults, and incorrect glycol mix.
Observable Symptoms
Faults manifest as poor hot water contribution, high collector temperatures, controller alarms, noisy circulation, or safety discharge.
External Root Causes
Most thermal faults originate from pressure control, degraded fluid, air in the loop, or incorrect settings rather than the collector itself.
Notes: Tutor depth:
Solar thermal systems can reach high temperatures. Maintenance issues may include degraded glycol, failed vessel, pump issues, air and stagnation. Work must follow manufacturer instructions and competence boundaries.
Reference in notes: Decerna discusses pressurisation and expansion vessel/glycol-related maintenance risks in solar thermal systems.
Tutor example
A customer reports that the solar thermal system is not helping to heat the hot water cylinder. On inspection, the controller shows a high collector temperature, but the cylinder temperature is not rising. This suggests that heat is available at the collectors, but it is not being transferred effectively.
Possible causes include a failed pump, air lock, blocked strainer, loss of pressure, degraded glycol, faulty sensor, failed expansion vessel or incorrect controller setting. The engineer should check system pressure, pump operation, flow, controller readings, glycol condition and fault history before replacing parts.
Learner takeaway
Solar thermal faults usually come down to three key questions: Is there enough pressure? Is the fluid able to flow? Is the heat transfer fluid in good condition?

## Slide 37: Solar thermal faults: overview (Slide 3 of 3)
3. Critical Failure Areas
Pressure and Expansion
Pressure loss allows air ingress, halting circulation. Faulty expansion vessels fail to manage fluid expansion, causing extreme pressure spikes.
Flow Rate and Overheating
Low flow due to air locks or pump failure leads to stagnation, severe collector overheating, rapid glycol breakdown, and system stress.
Controls and Sensors
Faulty sensors, damaged wiring, or incorrect configuration settings prevent the controller from triggering heat transfer at the correct times.
Notes: Tutor depth:
Solar thermal systems can reach high temperatures. Maintenance issues may include degraded glycol, failed vessel, pump issues, air and stagnation. Work must follow manufacturer instructions and competence boundaries.
Reference in notes: Decerna discusses pressurisation and expansion vessel/glycol-related maintenance risks in solar thermal systems.
Tutor example
A customer reports that the solar thermal system is not helping to heat the hot water cylinder. On inspection, the controller shows a high collector temperature, but the cylinder temperature is not rising. This suggests that heat is available at the collectors, but it is not being transferred effectively.
Possible causes include a failed pump, air lock, blocked strainer, loss of pressure, degraded glycol, faulty sensor, failed expansion vessel or incorrect controller setting. The engineer should check system pressure, pump operation, flow, controller readings, glycol condition and fault history before replacing parts.
Learner takeaway
Solar thermal faults usually come down to three key questions: Is there enough pressure? Is the fluid able to flow? Is the heat transfer fluid in good condition?

## Slide 38: Solar thermal: causes and symptoms (Slide 1 of 2)
1. Leaks in Solar Circuit
Causes: Failed seals, joints, stagnation stress. Symptoms: Pressure loss, glycol smell, fluid leakage.
2. Collector and Pipework Damage
Causes: Weather, freezing, UV, poor installation. Symptoms: Visible damage, degraded insulation, leaks.
3. Blockages and Restricted Flow
Causes: Degraded glycol, sludge, debris, air locks. Symptoms: High collector temp, poor cylinder heat gain.
4. Pump Failure / Poor Circulation
Causes: Electrical faults, seized pump, incorrect speed. Symptoms: No flow, high collector temp, pump noise/vibration.
5. Control System Failure
Causes: Failed sensors, loose wiring, bad controller settings. Symptoms: Pump fails to run, overheating, false temp readings.
Notes: Tutor note:
Use this as a fault map. Link each symptom to possible causes and what evidence would be gathered.
Prompt: why might solar thermal pump failure lead to overheating?
Tutor example
A customer reports that their solar thermal system is not contributing much hot water. The controller shows a high collector temperature but the cylinder temperature remains low. This suggests that heat is being collected but not transferred effectively.
Possible causes include pump failure, air lock, blocked strainer, degraded glycol, faulty sensor or incorrect controller settings. The engineer should check controller readings, pump operation, system pressure, flow, glycol condition and fault history before deciding whether the pump or another component is at fault.
Learner takeaway
Solar thermal faults often relate to pressure, flow, glycol condition and control operation. A high collector temperature with poor cylinder heating usually means the system is not moving or transferring heat correctly.

## Slide 39: Solar thermal: causes and symptoms (Slide 2 of 2)
6. Expansion Vessel Fault
Causes: Lost pre-charge, failed diaphragm, incorrect sizing. Symptoms: Extreme pressure spikes/drops, relief valve discharge.
7. Incorrect / Degraded Glycol
Causes: Weak mix (freezes), old/degraded fluid (sludge/acidic). Symptoms: Poor flow, reduced efficiency, burnt smell/dark fluid.
8. Stagnation and Overheating
Causes: Pump/power failure, no hot water demand, poor layout. Symptoms: High pressure, steam/noises, component stress.
9. Air in the Solar Circuit
Causes: Leaks, poor filling, failed automatic air vents. Symptoms: Gurgling noises, air locks, fluctuating pressure.
10. Poor Hot Water Contribution
Causes: Low solar gain, shading, high user expectations. Symptoms: No noticeable solar heating, low cylinder temp.
Notes: Tutor note:
Use this as a fault map. Link each symptom to possible causes and what evidence would be gathered.
Prompt: why might solar thermal pump failure lead to overheating?
Tutor example
A customer reports that their solar thermal system is not contributing much hot water. The controller shows a high collector temperature but the cylinder temperature remains low. This suggests that heat is being collected but not transferred effectively.
Possible causes include pump failure, air lock, blocked strainer, degraded glycol, faulty sensor or incorrect controller settings. The engineer should check controller readings, pump operation, system pressure, flow, glycol condition and fault history before deciding whether the pump or another component is at fault.
Learner takeaway
Solar thermal faults often relate to pressure, flow, glycol condition and control operation. A high collector temperature with poor cylinder heating usually means the system is not moving or transferring heat correctly.

## Slide 40: Scenario: ASHP low-flow and cold emitters
Reported Symptom
ASHP showing alarm; upstairs radiators staying cold.
Treat as a symptom, not an immediate diagnosis. The fault may be hydraulic, control, user, design, or component-related.
Next Steps and Action Route
Evidence to Gather
Ask when fault occurs (heating, DHW, cold weather)
Check system pressure, temperatures, ΔT, pump status
Inspect filters, strainers, valves, pipework, and leaks
Listen for air/cavitation; check fault codes and history
Action and Outcome
Correct simple issues (vent air, clean filters, balance)
Retest to confirm improved flow and temperatures
Record all findings or refer if specialist work is required
1. Possible System Causes
Air trapped in the heating circuit (especially upstairs emitters)
Low system pressure preventing stable circulation
Blocked strainer, magnetic filter, or heat pump filter
Closed or partially closed isolation, radiator, or bypass valves
Incorrect pump mode, speed, or flow setting
Poor balancing causing downstairs to take flow first
2. Low Carbon Design Causes
Undersized pipework restricting flow rate required by ASHP
Too many zones, TRVs, or actuators closing simultaneously
No suitable minimum flow route, bypass, buffer, or volumiser
Emitters too small for low-temperature operation
Poor hydraulic separation between heat pump and circuits
3. User and Control Causes
TRVs closed or set too low in upstairs rooms
Heating schedule too short for low-temperature heat pump run times
Thermostat used like a traditional boiler (frequent on/off changes)
DHW priority temporarily stopping space heating during cylinder reheat
Weather compensation or set-back settings misunderstood
4. Component Causes
Circulation pump not operating or not receiving correct signal
Motorised valve, actuator, or zone valve stuck closed
Flow sensor or pressure sensor giving incorrect info
Controller, wiring centre, or heat pump control fault
Blocked/failed component (valve, filter, pump, heat exchanger)
Notes: Tutor activity:
Learners create an evidence chain:
1) Questions to ask customer
2) Visual/listening checks
3) Operational readings
4) Potential tests
5) When to refer
Refer to Daikin example: minimum flow not guaranteed can generate a flow error on some models; always use model-specific manual.
Tutor example
A customer says the ASHP keeps alarming in the morning and the upstairs radiators are cold. The engineer checks the controller and finds a low-flow alarm. Instead of replacing the pump immediately, they check pressure, air, valve positions, filters, pump mode and zone status.
The system pressure is slightly low, the magnetic filter is restricted, and several upstairs TRVs are nearly closed. After cleaning the filter, restoring pressure within competence, opening the TRVs correctly and retesting, the upstairs radiators begin to heat. The flow/return ΔT improves and the alarm does not return.
Learner takeaway
A low-flow alarm does not automatically mean the heat pump has failed. In low carbon systems, flow faults often come from the wider heating system: pressure, air, filters, valves, zoning, emitters, controls or design.

## Slide 41: Preventing typical faults through maintenance (Slide 1 of 3)
Core Principle: Good maintenance reduces faults, but cannot correct poor design alone. If the root cause is poor design (e.g. undersized emitters, poor layout), maintenance may only reduce symptoms rather than fully solve the problem.
Notes: Tutor note:
Link to K1.42/K1.44/K1.45. Maintenance records allow trend analysis: pressure loss, increasing ΔT, repeated fault codes, worsening glycol condition or customer control changes.
Tutor example
A customer reports repeated low-flow faults on an ASHP. During maintenance, the engineer finds a blocked magnetic filter, low system pressure and several TRVs fully closed. The heat pump itself has not failed; the system conditions are preventing correct flow. The engineer cleans the filter, restores pressure within competence, explains suitable TRV use, retests flow/return temperatures and records the findings.
Learner takeaway
Maintenance is preventative fault-finding. It checks the system before failure occurs, identifies early warning signs, protects efficiency and helps customers use the system correctly.

## Slide 42: Preventing typical faults through maintenance (Slide 2 of 3)
Key System Checks
1. Water Quality and Protection
Check filters, strainers, inhibitor, and system pressure.
Poor water quality causes corrosion, sludge, and magnetite build-up, which blocks strainers and damages pumps/heat exchangers.
2. Controls and Sensors
Verify schedules, compensation, thermostats, and TRVs.
Incorrect settings cause comfort complaints and short cycling. Check controller fault history and firmware updates.
3. Emitters, Valves and Pumps
Inspect radiators, pumps, and safety expansion vessels.
Check emitters for cold spots/air, pumps for noise/vibration/leaks, and safety devices within guidance.
4. Outdoor and Source-Side
ASHP, GSHP, and solar thermal physical conditions.
Clean heat pump airflow path. Check brine lines, solar fluid quality, pressures, and signs of stagnation or glycol degradation.
Notes: Tutor note:
Link to K1.42/K1.44/K1.45. Maintenance records allow trend analysis: pressure loss, increasing ΔT, repeated fault codes, worsening glycol condition or customer control changes.
Tutor example
A customer reports repeated low-flow faults on an ASHP. During maintenance, the engineer finds a blocked magnetic filter, low system pressure and several TRVs fully closed. The heat pump itself has not failed; the system conditions are preventing correct flow. The engineer cleans the filter, restores pressure within competence, explains suitable TRV use, retests flow/return temperatures and records the findings.
Learner takeaway
Maintenance is preventative fault-finding. It checks the system before failure occurs, identifies early warning signs, protects efficiency and helps customers use the system correctly.

## Slide 43: Preventing typical faults through maintenance (Slide 3 of 3)
Maintenance Best Practices
Identify Trends, Not Just One-Off Faults
Compare current readings with service history.
Look for falling pressure or rising energy use patterns.
Trends reveal developing faults before breakdown occurs.
Educate Users to Prevent Repeat Faults
Teach correct schedule and thermostat control.
Advise against repeatedly topping up pressure silently.
Warn against blocking outdoor airflow or closing too many TRVs.
Record Evidence Clearly
Document all readings, water tests, and photo logs.
Strong logs protect warranties and aid future diagnosis.
Builds customer trust and guarantees compliance.
Notes: Tutor note:
Link to K1.42/K1.44/K1.45. Maintenance records allow trend analysis: pressure loss, increasing ΔT, repeated fault codes, worsening glycol condition or customer control changes.
Tutor example
A customer reports repeated low-flow faults on an ASHP. During maintenance, the engineer finds a blocked magnetic filter, low system pressure and several TRVs fully closed. The heat pump itself has not failed; the system conditions are preventing correct flow. The engineer cleans the filter, restores pressure within competence, explains suitable TRV use, retests flow/return temperatures and records the findings.
Learner takeaway
Maintenance is preventative fault-finding. It checks the system before failure occurs, identifies early warning signs, protects efficiency and helps customers use the system correctly.

## Slide 44: Recap checkpoint
01 Name the five main root-cause categories for faults.
02 Give three causes of lack of flow rate.
03 Why might an emitter have cold spots?
04 Give two typical heat pump faults requiring specialist referral.
05 Give three common solar thermal fault causes.
Notes: Suggested answers:
1) Poor installation, inadequate design, user error, environmental factors, component malfunction.
2) Blockage, air, low pressure, closed valve, pump issue, undersized pipe, dirty strainer.
3) Air, sludge, poor balancing, low flow, undersized emitter, closed valve.
4) Refrigerant leak, pressure trips linked to refrigerant circuit, PCB/manufacturer-only faults, fixed electrical safety issues.
5) Leaks, pump failure, control failure, expansion vessel losing pressure, incorrect glycol, blockages.
Wordwall/Quizizz recap created separately.

## Slide 45
Summary and questions
K1.43: Understanding root causes of typical faults, not just symptoms
Primary Root Cause Categories
Installation, design, user operation, environment, and component malfunction.
Wet Systems
Flow, pressure, water quality, and controls.
Heat Pumps
Hydraulic, electrical/electronic, refrigerant, sensors, or controls.
Solar Thermal
Pressure, glycol, pump/control operation, and stagnation.
Notes: Final tutor prompt: ask learners to complete the sentence: 'A symptom becomes useful when…'.

## Slide 46
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.