## Slide 1: Occupational specialism: Low Carbon Engineering PowerPoint K1.44: Fault finding techniques

## Slide 2: Introduction / starter
Warm-up
What is the first thing you should do when a customer reports 'the heat pump is not working’?
Pair-share
List three questions you would ask before touching the system.
Notes: Stop point: 3–5 minute discussion. Draw out safety, symptoms, recent changes, fault codes, controls, power, pressure, hot water/heating demand and when the problem started.

## Slide 3: Learning objectives
Identify fault-finding and diagnosis techniques used in low carbon systems.
Explain suitability of visual, listening, questioning, testing and digital diagnostics.
Apply a structured fault-finding approach in practical scenarios.
Recognise when multimeter/refractometer/component testing requires competence.
Use fault codes and software diagnostics without relying on them blindly.
Explain client/business implications when faults cannot be rectified.
Notes: Learners should understand the method and decision-making process, not just memorise fault-finding tools.

## Slide 4: Fault-finding mindset: structured diagnosis
01. Make safe first
Identify hazards and isolate supplies before beginning. Stay within competence.
02. Question the client
Ask about noises, smells, or recent changes like maintenance or power cuts.
03. Gather evidence
Check fault codes and visual clues before replacing parts to save time and cost.
04. Start simple
Rule out low pressure, closed valves, or air before assuming component failure.
05. Use instructions
Follow manufacturer fault trees and service data to protect the system warranty.
06. One change at a time
Change one thing then retest to identify exactly what fixed the fault.
07. Record findings
Document codes, readings, and actions to support communication and future visits.
08. Refer out of scope
Stop and refer if the fault involves refrigerants or work outside your competence.
Notes: Tutor note:
Stress: diagnosis is not guessing. Random part replacement increases cost, damages trust and may miss safety issues.
Tutor example
A customer reports that the heat pump “keeps stopping”. Instead of assuming the compressor has failed, the engineer asks questions first. The customer explains that the fault normally happens in the morning, the upstairs radiators stay cool, and the system has recently had a filter cleaned.
The engineer checks the fault history and finds a low-flow fault code. Visual inspection shows one isolation valve is not fully open, and the system pressure is low. After correcting the valve position, topping up/venting within competence, and checking flow/return temperatures, the fault clears. The engineer records the customer comments, checks, readings and final result.
Learner takeaway
Good fault-finding is not guessing. It is a structured process: make safe, ask questions, gather evidence, check simple causes, follow manufacturer guidance, test carefully, record clearly and refer when required.
Simple structure: Reported symptom → safety check → questions → visual/listening checks → readings/tests → manufacturer fault tree → action/repair/escalation → record.

## Slide 5: Suitability of fault-finding techniques
01. Visual inspection
Best for obvious defects and installation
Identify leaks, corrosion, damage, and blocked components. Best for first attendance and pre-test checks.
02. Listening
Useful for noise and flow-related faults
Detect cavitation, air, and fan/valve noise. Use as a clue to confirm with further inspection.
03. Questioning
Essential for history and intermittence
Ask about timings, weather, and changes. Vital for intermittent and control issues.
04. Testing
Confirms evidence (competence req.)
Measurable data: voltage, pressure, flow. Proves repairs and manufacturer compliance.
05. Digital Diagnostics
Fault codes and live performance
Apps and service tools show trends and histories. Codes guide the area of investigation.
06. Escalation
When fault is outside scope
Required for regulated/safety work (refrigerants, fixed electrics) or design failures.
Best Practice: Combine Techniques
Effective diagnosis uses several methods together. Example: A low-flow code may trigger questioning, visual valve checks, and listening for pump noise.
Notes: Tutor depth:
No single technique diagnoses every fault. Learners should combine techniques and choose based on the symptom, risk and evidence available.
Tutor example
A customer reports that the ASHP is noisy and heating is poor.
A structured approach might include:
Questioning: When does the noise happen — start-up, defrost, DHW, heating, or night-time?
Visual inspection: Check outdoor unit, pipework supports, valves, filters and clearances.
Listening: Identify whether the noise is pump, fan, vibration, air or pipe velocity.
Testing: Check system pressure, flow/return temperatures, pump operation and flow rate where possible.
Software/fault codes: Check fault history and live data.
Escalation: Refer if the fault points to electrical, refrigerant or design issues outside competence.
Learner takeaway
The right technique depends on the symptom, risk and competence required. Good diagnosis uses evidence from questioning, inspection, listening, testing and software data before deciding whether to repair, adjust, replace or escalate.
Stop point: match technique to symptom activity.

## Slide 6
Visual inspection checklist
01. General and Mechanical
General Condition
Look for leaks, corrosion, damage, missing insulation, vibration, or overheating. These indicate poor install or stress.
Valves, Filters and Pumps
Check valve positions (isolation, zone, bypass).
Inspect filters for blockage or leaks.
Check pumps for leaks, wiring, and orientation.
02. Specific Heat Sources
ASHP
Check airflow, blocked grilles, ice build-up, and drainage/pooling risk.
GSHP/WSHP
Inspect brine pipework, manifolds, and heat exchangers for leaks or fouling.
Hybrid/Bivalent
Verify connections between sources and switchover controls.
Sensors and Wiring
Look for loose sensors, poor placement, or water ingress risks. Do not open unless authorised.
03. Distribution and Data
Storage and DHW
Inspect cylinders, buffer vessels, and PRVs for leaks or signs of discharge.
Emitters
Check radiators and UFH manifolds for cold zones or air vents.
Record and Decide
Use clues to decide next tests (e.g. blocked strainer → flow check).
Record component, location, and findings. Take photos for evidence.
Notes: Tutor note:
Visual inspection should not be dismissed as basic. Many faults are visible: closed valves, blocked coils, frozen condensate routes, dirty filters, loose sensors, incorrect labels, missing insulation.
Tutor example
A customer reports poor heating from a ground source heat pump. Before assuming the heat pump has failed, the engineer visually checks the plant room and finds the brine manifold pressure appears low, one valve is partly closed, and insulation is damaged on a section of source pipework. These findings guide the next steps: checking pressure, flow, glycol/brine concentration and manufacturer fault guidance before replacing any components.
Learner takeaway
Visual inspection is not just “looking around”. It is a structured fault-finding technique that helps identify clues, prioritise testing and decide whether the fault can be corrected, tested further or referred to a competent specialist.
Prompt: what visible clue might explain poor flow? Blocked strainer, closed valve, air vent issue, kinked flexible hose, sludge.

## Slide 7: Listening for unusual noises
01. Pumps
Whine, cavitation, vibration or intermittent operation.
02. Pipework
Water hammer, air movement, high velocity noise or rattles.
03. Fans/Outdoor Unit
Scraping, vibration, obstruction or bearing noise.
04. Valves/Actuators
Clicking, buzzing or failure to move.
Investigation Protocol
Noise is a clue – confirm with readings and inspections.
Stop if noise suggests unsafe mechanical/electrical failure.
Notes: Tutor depth:
Noise can be customer-reported and intermittent. Ask when it happens: heating, DHW, defrost, pump start-up, zone changeover, night-time, high wind.
Mini example: gurgling + cold emitters may suggest air/low pressure; pump whine + high ΔT may suggest restriction or cavitation.

## Slide 8: Asking questions: diagnostic interviewing
01. The Basics
Ask what changed and when it started
Is it affecting heating, DHW, or both?
02. System and History
Controls: Schedules, setpoints, boosts, apps, and error messages
Recent Work: Service, power cut, pressure top-up, or building changes
03. Identifying Patterns
Cold weather triggers
Morning issues
After showers
After defrost cycles
Communication Protocol
Use plain language and avoid blaming the customer.
Confirm understanding by summarising the fault back to the customer.
Notes: Tutor note:
Good questions save time. A fault reported as 'no heating' may be schedule error, low pressure, no demand, tripped supply, DHW priority, lockout or customer expectation issue.
Activity: learners create 8 diagnostic questions for a 'no hot water' complaint.

## Slide 9: Questioning examples: symptom to clue
01. No heating
Is the controller calling for heat? Any zones affected?
02. No hot water
Was DHW boost used? Is there a scheduled reheat?
03. High bills
Have flow temperatures, schedules or immersion settings changed?
04. Noise
When does it happen – pump, fan, defrost or zone change?
05. Intermittent fault
What time/weather/load conditions trigger it?
06. Fault after service
What was changed, cleaned, reset or isolated?
Notes: Tutor guide:
Ask learners to avoid leading questions. Better: 'What did you notice first?' rather than 'Did you press the wrong button?'
Customer communication link: explain that questions are part of diagnosis, not interrogation.

## Slide 10: Multimeter testing: suitability and limits
01. Measurements
Voltage, continuity, and resistance.
Confirm electrical supply, sensors, and component circuits.
02. Supply and Control Checks
Check power to controllers, pumps, and actuators.
Verify fuse continuity and open/closed circuits.
03. Sensors and Components
Test resistance vs. manufacturer tables.
Confirm component supply voltage before replacement.
04. Safety and Competence
Only trained, authorised persons should test.
Refer fixed wiring/board work to electricians.
05. Isolation and Live Testing
Safe isolation is critical before resistance tests.
Live testing restricted to necessary scenarios.
06. Equipment and Recording
Leads/meter must be in good condition.
Record actual values; do not write "tested OK“.
Critical Safety Warning
Testing resistance on an energised circuit can damage the meter, damage equipment, and create significant danger. Always follow correct safe isolation procedures.
Notes: Tutor depth:
Keep this within competence boundaries. Low carbon engineers may need awareness of what multimeter testing can prove, but electrical testing may need electrician/authorised person.
Tutor example
A heat pump shows a cylinder temperature sensor fault. The engineer does not immediately replace the sensor. First, they check the manufacturer fault tree and isolate the circuit safely. The sensor resistance is measured and compared with the manufacturer’s resistance/temperature table. If the resistance is outside the expected range, the sensor may be faulty. If the sensor reading is correct, the issue may be wiring, connection, controller input or sensor placement.
Learner takeaway
A multimeter is a diagnostic tool, not a guessing tool. It helps confirm evidence, but electrical testing must be completed safely, within competence and against manufacturer values.
Examples: checking a sensor resistance against temperature chart; checking a pump has supply; checking a fuse/continuity after safe isolation.

## Slide 11: Multimeter testing: what may be checked
01. Voltage testing
Checks whether the correct supply or control voltage is present at a component (e.g. pump, controller, actuator).
02. Continuity testing
Checks for a complete path in a circuit or fuse. Must be done with the circuit safely isolated.
03. Resistance testing
Used for sensors, thermistors, or coils. Compare readings with manufacturer data.
04. Polarity checks
Confirms L, N, and E connections are correct. Must only be carried out by a competent person.
05. Earth continuity
Confirms the protective earth path is present. Specialist safety work for competent persons.
06. Insulation resistance
Specialist electrical testing for fault investigation. Must be done by an authorised competent person.
Notes: Tutor depth:
Keep this within competence boundaries. Low carbon engineers may need awareness of what multimeter testing can prove, but electrical testing may need electrician/authorised person.
Examples: checking a sensor resistance against temperature chart; checking a pump has supply; checking a fuse/continuity after safe isolation.

## Slide 12: Refractometer testing: glycol/brine concentration
01. How it Works
Measures solution concentration by checking how light bends through the fluid sample.
Confirms fluid mixture provides required frost protection.
02. Key Applications
Ground Source Heat Pumps:
Brine loops in ground collectors or boreholes.
External Pipework:
Monobloc circuits or any frost-protected circuits.
03. Critical Risks
Low Concentration: Risk of freezing, burst pipes, and damage.
High Concentration: Increases viscosity, reduces flow rate, and heat transfer efficiency.
04. Testing Protocol
Check sample for contamination, debris, and discolouration.
Ensure use of correct scale (ethylene vs. propylene glycol).
05. Requirements
Compare results with manufacturer and design specifications.
Required mix depends on system design, climate, and fluid type.
06. Evidence and Action
Record concentration, temp, date, and tester name.
Note if system requires dilution, top-up, or flushing.
Notes: Tutor note:
Refractometer testing is a water/fluid quality diagnostic technique. Too little glycol may freeze; too much can reduce flow and heat transfer.
https://www.youtube.com/watch?v=b7wG_Fg1Iss
Tutor example
A ground source heat pump is showing repeated source-side low-flow faults in cold weather. The engineer checks the brine circuit and uses a refractometer to test the fluid concentration.
The result shows the glycol concentration is much higher than the design requirement. The fluid is over-protected against freezing but has become more viscous, meaning the pump has to work harder to circulate it. This can reduce flow rate and heat transfer, causing poor performance or low-flow alarms.
The correct action is not simply to increase pump speed. The engineer should compare the reading with the manufacturer/design requirement, check pressure and flow, record the result, and arrange correction within competence.
Learner takeaway
Refractometer testing proves whether the frost-protection fluid is suitable. The aim is not “as much glycol as possible” — the aim is the correct concentration for frost protection, flow rate, pump performance and heat transfer.
Mini scenario: GSHP low source-side flow fault. Refractometer shows excessive glycol concentration, causing high viscosity and pump strain. Escalate/design check may be needed before dilution/top-up.

## Slide 13: Component testing
01. The Basics
Tests one component to confirm it operates correctly and performs its intended function.
02. Common Components
Pumps, actuators, valves, sensors, thermostats, and control relays. Note: faults can manifest elsewhere.
03. Manufacturer Procedures
Follow service manuals and expected values (voltage, resistance, flow). Don't judge by appearance alone.
04. Root Cause Analysis
Confirm the component is the cause. Issues like air locks or wiring can mimic component failure.
05. Operating Conditions
Check power signals, pressure, and demand. Components cannot work if surrounding conditions are wrong.
06. Safety First
Never bypass safety devices or logic. Unauthorised bypassing creates hazards and voids warranties.
07. Evidence-Based Replacement
Replace only when testing or guidance proves fault. Address root causes like water quality or wiring first.
08. Records and Documentation
Record test method, actual vs. expected values, and results. Clear records support warranty and communication.
Notes: Tutor depth:
Component testing should follow evidence. Example: pump not running could be failed pump, no control signal, failed relay, airlock, seized impeller, tripped supply, or controller setting.
Tutor example
A heat pump shows a low-flow fault. The engineer might suspect the circulation pump, but should not replace it immediately.
A structured component test would check:
Is there a heating or DHW demand?
Is the pump receiving the correct control signal?
Is the pump powered?
Are isolation valves open?
Is the system pressure correct?
Are strainers or filters blocked?
Is there air in the system?
Does the pump operate in the correct mode/speed?
What is the flow/return temperature difference?
If the pump has power and signal but does not run, it may be faulty. If the pump runs but flow remains poor, the fault may be a restriction, air, pipework issue or balancing problem.
Learner takeaway
Component testing is about proving cause, not guessing parts. Before replacing a component, confirm that the system conditions, controls and manufacturer values support the diagnosis.
Prompt: why is it risky to replace a pump without confirming power/control signal and hydraulic restriction?

## Slide 14: Software diagnostics and remote monitoring
01. Access Tools
Uses controller menus, service tools, apps, manufacturer portals, or cloud platforms.
02. Live System Data
Shows flow/return temps, flow rates, compressor status, and pump operation to understand real-time performance.
03. History and Trends
Reveals fault history, run hours, defrost activity, and energy trends — critical for intermittent faults.
04. Pre-visit Triage
Helps engineers prepare tools and parts before site attendance, reducing unnecessary visits for simple setting issues.
05. Aftersales Support
Dashboards allow manufacturers to review fault codes and system data to support warranty decisions.
06. Permissions and Privacy
Requires customer consent and secure handling of data, location information, and usage patterns.
07. Interpretation Rule
Data alone is not a diagnosis. It must be paired with questioning, inspection, and manufacturer guidance.
08. On-site Confirmation
Safety-critical decisions or repairs MUST be confirmed with appropriate on-site checks (e.g. ΔT vs. actual flow).
09. Record Evidence
Log codes, timestamps, and readings to support warranty claims and future fault-finding efforts.
Notes: Tutor note:
Software diagnostics are increasingly important for heat pumps. They can show whether a fault is controls, flow, temperature, sensor or compressor related.
Tutor example
A customer reports that their ASHP “randomly stops overnight”. Remote monitoring shows repeated low-flow alarms occurring during DHW reheat. The data also shows high flow temperatures and frequent compressor starts.
Before replacing components, the engineer uses this information to plan the visit. On site, they check the cylinder demand, pump operation, filters/strainers, system pressure and valve positions. A partially blocked strainer is found, cleaned and retested. The engineer records the remote fault history, on-site findings and corrected readings.
Learner takeaway
Remote monitoring helps guide diagnosis, but it does not replace good fault-finding. Use software data to identify patterns and prepare for site visits, then confirm the cause through safe on-site checks, manufacturer guidance and recorded evidence.
Ask learners: what data would be useful before attending a 'high running cost' complaint? Flow temp, immersion run time, DHW boosts, weather comp, starts/stops, fault history.

## Slide 15: Fault codes: useful but not the full diagnosis
01. Investigation and Manufacturer Guidance
Fault codes are a starting point, not proof of failure.
Always check manufacturer-specific installation/service manuals for exact codes and diagnostic sequences.
02. Recording and History
Record the exact code, conditions (date/time, mode, temps), and live data (flow rates, pressures).
Check repeat patterns and history; don't just look at the latest alarm.
03. Action and Escalation
Clear codes only after investigation, corrective action, and retesting.
Escalate issues outside competence, such as sealed circuits or fixed electrical safety, to technical support.
Example: "Low Flow" Code
May be caused by: blocked strainer, air, low pressure, closed valve, pump issue, flow sensor issue, or poor system design. Skipping diagnostic steps can lead to replacing the wrong component.
Notes: Tutor depth:
Example: a 'low flow' code could be pump fault, air, closed valve, blocked strainer, low pressure, undersized pipework or sensor issue. Do not replace the flow sensor without checking the hydraulic causes.
Manufacturer example
A Daikin installer reference guide gives an example where, if the minimum water flow is lower than the required value, the unit may stop operation and display error 7H-01. This code points toward a water flow issue, not automatically a failed flow sensor. The diagnostic route should consider hydraulic causes such as pump operation, air, blocked filters/strainers, closed valves, bypass settings or restricted flow before replacing components.
Tutor example
A heat pump displays a 7H-01 water flow fault. A weak diagnosis would be: “The flow sensor has failed — replace it.”
A structured diagnosis would be:
Ask when the fault occurs: heating, DHW, start-up, or after zones close.
Check system pressure and air in the circuit.
Check isolation valves and zone valves are open when demand is present.
Check filters/strainers for blockage.
Check pump operation and pump setting.
Check flow/return temperatures and available flow-rate data.
Only then consider sensor, wiring or PCB faults if the evidence supports it.
Learner takeaway
A fault code is a clue, not a conclusion. Use it with manufacturer guidance, customer questioning, visual inspection, live readings and safe testing before deciding whether to adjust, repair, replace or escalate.
Stop point: fault code → possible causes activity.

## Slide 16: Combining techniques: evidence chain
Reported symptom: customer says upstairs radiators are cold.
Initial Assessment: Treat comment as a symptom, not diagnosis. Could be air, balancing, pressure, valves, pump, zoning, filters, or design.
Step 1: Ask Focused Questions
Which radiators are cold?
When does it happen (mornings, DHW)?
Recent changes or fault codes?
Step 2: Visual and Listening Checks
Check TRVs and zone valves.
Listen for pump noise/cavitation.
Look for leaks or air vents.
Step 3: Gather Operational Data
Record flow/return temps (ΔT).
Check system pressure and pump mode.
Verify zone status/priority mode.
Step 4: Interpret Evidence
High ΔT = Low flow/blockage.
Gurgling = Air ingress.
Only cold during DHW = Priority mode.
Step 5: Component Testing
Only test actuators/pumps if evidence points there.
Perform electrical tests via manufacturer procedure.
Step 6: Correct, Retest and Record
Correct issues (vent air, clean strainer, balance).
Retest and record. If design failure or electrical fault, stop and refer.
Notes: Tutor guide:
Use this slide to show an evidence chain. Each step narrows the cause. Encourage learners to ask: 'What evidence would confirm or rule out this cause?'
Tutor example
A customer reports that the upstairs radiators are cold. The engineer asks questions and finds the issue is worse in the morning. Visual inspection shows the downstairs radiators heat quickly, but upstairs radiators remain cool. The system pressure is slightly low, and the flow/return temperatures show a larger-than-expected ΔT.
The engineer vents air from the upstairs radiators, checks the strainer, confirms the pump mode, and balances the downstairs radiators so they do not take too much flow. After retesting, the upstairs radiators heat more evenly, ΔT moves closer to design intent, and the final readings are recorded.
Learner takeaway
An evidence chain links the symptom to the cause. Good fault-finding moves logically from customer questions, to inspection, to readings, to targeted testing, then correction and retest. This avoids guessing, unnecessary part replacement and repeat call-backs.

## Slide 17: Scenario 1: low-flow fault code
Symptom: ASHP displays low-flow fault after installation.
Possible causes:
Air locks in system
Closed valves or blocked strainer
Incorrect pump setting
Low system pressure
First checks:
System pressure gauge
Valve positions and venting
Check strainers for debris
Verify pump operation
Evidence to gather:
Check flow/return ΔT, controller flow data, pump mode, and unusual noises.
Actions:
Correct within competence levels. Always retest the system and record findings.
Escalate: Suspected design/pipe sizing issues or manufacturer fault.
Notes: Suggested learner output:
Write a 6-step diagnostic plan. Include at least one question, one visual check, one operational reading and one record entry.
Key: do not assume the flow sensor has failed just because a flow code appears.

## Slide 18: Scenario 2: high running cost complaint
Symptom: customer reports electricity use is much higher than expected.
Diagnostic questions:
Schedules and setpoints
DHW boosts and immersion use
Energy tariff details
Recent changes to usage
Check controls and operation:
Weather comp and setback strategy
Flow temp and DHW priority
Cycling and emitter distribution
Review fault history
Check design evidence:
Verify heat loss calculations, emitter sizing, and refer to handover guidance documentation.
Key actions:
Adjust settings within competence. Retest system and communicate findings clearly to the customer.
Escalate: If issues relate to original design or unmanageable customer expectations.
Notes: Tutor note:
High running cost is often multi-factorial. It may be user settings, high flow temps, poor building fabric, undersized emitters, tariff, immersion use, poor balancing or unrealistic expectations.
Communication link: be transparent without blaming the customer.

## Slide 19: Scenario 3: poor DHW recovery
Symptom: cylinder is slow to reheat or hot water runs out quickly.
Diagnostic focus:
Questions: usage, changes, boost, time
Visuals: sensor, valves, pump, TMV
Secondary circulation check
Operational data:
Cylinder setpoint and flow temp
DHW priority settings
Immersion/boost usage
Review system alarms
Possible causes:
Small coil, control setting errors, failed sensor, high demand, or scaling/sludge issues.
Key actions:
Explain recovery limits to user. Adjust and check settings within your competence.
Escalate: Escalate to design team if underlying issues are suspected.
Notes: Tutor depth:
Heat pump DHW recovery differs from boilers. Fault-finding must separate system fault from design limitation or usage mismatch.
Prompt: what evidence would show a design issue rather than a component failure?

## Slide 20: When faults cannot be rectified: decision routes
Compliance mandate: Engineers must not continue operation if it breaches safety, legal, or manufacturer requirements.
1. Component Replacement
Required if repair is impractical, unsafe, or not cost-effective.
Pumps, actuators, sensors, valves
Controllers, expansion vessels
Based on evidence and mfr guidance
2. System Replacement
Best option for repeated faults, obsolescence, or poor reliability.
Beyond economic repair
Unable to meet needs safely
3. System Upgrade
Redesign needed for root design or compatibility issues.
Undersized emitters or pipes
Poor hydraulic layout
Unsuitable controls/cylinder
4. Temporary Solution
Maintain essential heating/hot water while arranging works.
Safe and permitted adjustments
Backup heat or immersion use
Must NOT bypass safety devices
5. Decommissioning
Necessary if system presents serious safety risks.
Unsafe electrical/gas conditions
Failed pressure components
Refer to competent person
6. Communication and Evidence
Essential for transparency and protecting all parties.
Inform customer of risks/costs
Record symptoms and test results
Evidence supports the route
Notes: Tutor note:
Faults cannot always be fixed on the visit. Learners must understand implications for customer and business. Avoid promising immediate repair if parts, specialist support or design changes are needed.
Tutor example
A heat pump repeatedly shows low-flow faults even after the filter has been cleaned and the pump has been checked. Further investigation shows that the pipework is undersized and several emitters are too small for low-temperature operation. In this case, replacing the pump again would not solve the problem. The correct decision route may be a system redesign or upgrade, supported by recorded evidence and clear communication with the customer.
Learner takeaway
When a fault cannot be rectified, the engineer must move from “fixing the fault” to making a safe, evidence-based decision: replace, upgrade, provide a safe temporary solution, decommission, or refer.

## Slide 21: Replacement of components or system
Compliance mandate: Engineers must not continue operation if it breaches safety, legal, or manufacturer requirements.
Evidence-based Replacement
Components should only be replaced when fault-finding confirms failure or non-operation within limits.
Avoid "guessing" to prevent cost and disruption
Confirm diagnosis (fault codes, live data, etc.)
Compatibility and standards
Parts must suit system design, manufacturer requirements, and operating conditions.
Use approved/genuine parts for warranty
Check voltage, flow, control signals, etc.
Full system replacement
Required if equipment is obsolete, unsafe, beyond economic repair, or repeatedly failing.
Consider where repair cost > replacement
Check if design is the root cause
Customer communication
Cost and disruption: Explain parts, labour, lead times, and disruption clearly.
Warranty: Explain validity, installer requirements, and conditions.
Recording and records
Pre-work: Record diagnosis, evidence, quotation, and approval.
Post-work: Record serial numbers, test results, and final readings.
Typical components
Pumps, zone valves, actuators, sensors, thermostats, expansion vessels, PRVs, filters, magnetic filters, immersion elements.
Notes: Tutor depth:
Replacing components without diagnosis damages trust and profitability. If a component fails because of sludge, poor flow or design, replacing it may not solve the root cause.
Tutor example
A heat pump shows repeated low-flow faults. The engineer suspects the circulation pump, but before replacing it they check pressure, air, valve positions, strainer condition, pump signal and flow/return temperatures. The pump is receiving the correct signal but is not operating correctly. The manufacturer confirms the replacement part number and warranty process. The engineer provides the customer with a quote, lead time and expected disruption before replacing the pump and retesting the system.
Learner takeaway
Replacement should be the result of diagnosis, not a shortcut around it. The engineer must prove the fault, check compatibility, protect warranty, communicate clearly with the customer and record approval before proceeding.
Ask learners: what evidence would you want before replacing a circulation pump?

## Slide 22: System upgrade
Core drivers and rationale
When is an upgrade required?
When equipment functions but design prevents required performance. Simple part replacement won't solve root causes like sizing or strategy.
Consequences of design limits:
Repeat faults / poor performance
High running costs / frequent cycling
Cold rooms / long warm-up times
Excessive backup heating use
Upgrade categories
Emitters and hydraulics
Larger radiators, underfloor adjustments, pipework resizing, or improved pump selection.
Hot water and controls
Heat pump compatible cylinders (larger coils) and weather compensation or smart controls.
Electrical
Supply changes, isolators, or backup heater wiring by a competent person.
Process and evidence
Evidence-based justification
Use heat loss calcs, flow/return temps, and pressure readings. Do not base on opinion alone.
Customer engagement
Explain impact on comfort/cost
Record options and approvals
Document consequences of refusal
Compliance Mandate: Engineers must ensure upgrades are evidence-based and clearly documented for customer safety and system reliability.
Notes: Tutor note:
System upgrade is not a 'fault repair' in the narrow sense; it addresses a suitability/design issue. Link to K1.17/K1.20 science and K1.15 controls.
Tutor example
A customer reports that their home never reaches the desired temperature on cold days, even though the heat pump is running continuously. Fault-finding shows no failed components, but the radiators are too small to heat the rooms at the designed low flow temperature. Increasing the flow temperature would make the system less efficient and more expensive to run.
In this case, the correct route may be a system upgrade, such as larger radiators, improved balancing and revised controls, rather than replacing the heat pump or pump.
Learner takeaway
A system upgrade is needed when the fault is caused by the design, not a failed part. The engineer must prove this with evidence, explain the options clearly, and record the customer’s decision before any change in scope.

## Slide 23: Temporary solutions
Purpose and Scope
Used to maintain essential services while waiting for parts or specialist support.
Operational Boundaries:
Must be safe, legal and within manufacturer/competence boundaries
Must not bypass safety devices or hide serious defects
Typical Examples
Safe temporary control settings
Backup heater use
Partial zone operation
Engagement and Records
Explain limitations, running cost impact, and expected duration to the customer.
Required Actions:
Record customer agreement
Document follow-up plan
Compliance mandate: Temporary solutions must never compromise safety or legal requirements and must be clearly explained and recorded.
Notes: Tutor depth:
Temporary solutions can help customers, but they carry risk if poorly explained. Example: using immersion backup may restore DHW but increase electricity cost. A temporary setting must not become the permanent fix without review.
Prompt: what temporary solution would be unacceptable? Bridging safety device, running unsafe equipment, ignoring refrigerant leak.

## Slide 24: System decommissioning and compliance
Criteria for decommissioning
When is it required?
Required where operation is unsafe, illegal, or likely to cause damage.
System cannot be operated safely
Risk to person, property, or equipment
Specialist requirements
Certified Personnel Only
F-Gas certified (Refrigerants)
Competent electrician (Fixed wiring)
Gas Safe / OFTEC registered
Stay within scope of competence
Legal and regulatory
Compliance Rules
Adhere to Building Regs, water regs, and environmental controls.
Correct handling of glycol/brine
Safe disposal of hazardous parts
Unsafe systems
Mandatory Actions
Isolate component; switch off
Prevent automatic restarts
NEVER bypass safety devices
Label issue and advise customer
Communication
Customer Transparency
Clear, factual, non-technical
Explain why it is unsafe
Outline next steps and referrals
State impact on heat/water
Evidence and records
Essential Documentation
Faults, risks, and test results
Notices issued and isolation actions
Date, time, and acknowledgements
Protect customer and engineer
Compliance mandate: Decommissioning must be supported by evidence, clear communication, and referral to competent specialists where required.
Notes: Tutor note:
Do not give procedural decommissioning steps for regulated systems. Keep focus on when it may be required and the need for competent persons.
Tutor example
An engineer attends a heat pump system with poor hot water performance. During inspection, they notice that the unvented cylinder discharge pipework appears incorrectly installed and there are signs that the temperature and pressure relief valve has discharged. The engineer should not ignore this to keep the system running.
The correct route is to make the situation safe within competence, advise the customer not to use the unsafe arrangement, record the findings, and refer the work to a competent unvented hot water person. If necessary, the affected part of the system should be isolated until it has been inspected and corrected.
Learner takeaway
Decommissioning is not a failure to repair — it is a safety and compliance decision. When continued operation is unsafe or non-compliant, the engineer must make safe, communicate clearly, record evidence and refer to the correct competent person.
Link to K1.8 competence boundaries and K1.41 documentation.

## Slide 25: Communication and transparency
Clarity of language
Explain findings in plain language, supported by evidence.
Be clear about what is known, what is suspected and what needs further testing.
Actionable options
Explain options:
Repair or replace
Upgrade or temporary solution
Decommission
Impact statements
State implications regarding:
Time, cost, and disruption. Warranty and compliance implications.
Professional conduct
Avoid blame and avoid over-promising.
Evidence and records
Record customer decisions, approvals and declined recommendations.
Compliance mandate: Effective communication must be supported by evidence and documented decision-making.
Notes: Tutor depth:
Good fault-finding includes communication. Customers may be stressed if heating/hot water is unavailable. Ethical communication reduces disputes.
Role-play: explain a failed pump diagnosis and parts delay to a customer.

## Slide 26: Refund or compensation: business implications
Service Performance
When issues arise
Performance below reasonable expectation
Poor workmanship or repeat faults
Incorrect diagnosis or unsuitable products
Consumer Law
Consumer Rights Act 2015
Services: Reasonable care and skill
Goods: Satisfactory quality and fit for purpose
Remedies: Repeat performance or price reduction
Records and Evidence
Handling Complaints
Use company formal procedures
Record facts to determine responsibility
Include: Quotations, test results, photos
Possible Outcomes
Remedial work or replacement parts
Goodwill gesture or partial refund
Formal compensation or insurance referral
Communication
Keep it professional and factual
Avoid blame or defensive language
Listen, record, and escalate properly
Authorisation
Crucial Limit
NEVER promise compensation unless authorised
Escalate safety or legal issues promptly
Compliance mandate: Business implications must be managed through formal procedures, factual records, and authorised professional communication.
Notes: Tutor note:
Keep this awareness-level and not legal advice. Link to business risk and evidence. Good records protect the customer and business by showing what was agreed, installed, tested and explained.

## Slide 27: Recap checkpoint
Why should you ask questions before testing?
What can a fault code tell you, and what can it not prove?
Give one use of a refractometer in heat pump systems.
Why must component replacement be evidence-based?
Name two options when a fault cannot be rectified immediately.
Be prepared to discuss your answers with the group.
Notes: Suggested answers:
1) Questions reveal history, patterns, settings and recent changes.
2) It points to an area; it does not always prove the failed component.
3) Checking glycol/brine concentration for freeze protection/flow impact.
4) Avoid unnecessary cost and missing root cause.
5) Temporary solution, replacement, upgrade, decommission, referral/specialist support.
Wordwall/Quizizz recap created separately.

## Slide 28
Knowledge check / summary
Use visual inspection, listening, questioning, testing, and diagnostics together.
Fault codes and software data need interpretation and evidence.
Always work within competence and manufacturer instructions.
When faults cannot be rectified, communicate options, cost, time, and compliance implications.
Notes: Final tutor prompt: ask learners to complete the sentence: 'Good fault-finding is…'.

## Slide 29
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.