## Slide 1
Occupational Specialism: Plumbing & Heating Engineering
K1.7 Plumbing and heating systems
K1.8 Components used in plumbing and heating systems
Fully pumped heating systems: S Plan+, Y Plan, W Plan

## Slide 2: Starter
Warm-up:
Why do modern heating systems use motorised valves and pumped circulation rather than relying on gravity flow?

## Slide 3: Objectives
You should be able to:
Describe fully pumped heating systems and their operation
Explain S Plan+, Y Plan and W Plan layouts
Understand zoning and control principles
You might also be able to:
Compare diverting and mid-position valve functions
Identify components in live or schematic systems
Sketch and label system layouts

## Slide 4: Introduction to fully pumped systems
Fully pumped systems use a circulator to move heated water from the boiler to radiators and hot water cylinders. This design improves efficiency, heat distribution, and control.
Motorised valves direct the flow of water depending on heating or hot water demand. By using pumps and valves, the system delivers faster response, greater comfort, and energy savings compared to older gravity-based systems.

## Slide 5: Overview of control valves
Two-port motorised valves used in S Plan and S Plan+.
Three-port motorised valves used in Y and W Plans.
Valves direct or divert water flow.
Controlled by electrical signals from timers and thermostats.
Essential for zoning and sequencing.
Question: What advantage do motorised valves give compared to uncontrolled circulation?

## Slide 6: S Plan system
The S Plan system is a fully pumped central heating arrangement that uses two-port motorised valves to control hot water and heating circuits independently. Each valve is operated by its own thermostat and programmer channel, allowing separate control of domestic hot water and space heating.
When a thermostat calls for heat, the corresponding valve opens and activates a microswitch, which signals the boiler and pump to run. This design provides flexibility, as heating and hot water can operate together or separately, and additional zones can be added easily in an S Plan+ arrangement.
The system is reliable, energy-efficient, and widely used in modern domestic installations.

## Slide 7: S Plan+ system
The S Plan+ system uses three two-port motorised valves, typically one for hot water and one or more for heating zones. Each valve is independently controlled by its own thermostat and programmer channel.
When a thermostat calls for heat, its valve opens, activating a microswitch that signals the boiler and pump to run.
This arrangement allows multiple zones and provides excellent flexibility in modern installations.

## Slide 8: S Plan+ components
Boiler and pump.
Three two-port motorised valves.
Cylinder thermostat.
Room thermostat(s).
3 channel Programmer/timer.
Hot water cylinder.
Question: Why does each S Plan+ zone need its own two-port valve?

## Slide 9: Zoning in S Plan+
Zoning means dividing the heating system into separate controllable areas. For example, ground floor radiators, first floor radiators, and domestic hot water may each be on different valves.
This improves comfort and efficiency by only heating the required zones.
Zoning also reduces energy costs and allows independent control of temperature and schedules in different areas of the property.

## Slide 10: Y Plan system
The Y Plan uses a single three-port mid-position valve to control flow between central heating and hot water. The valve can direct water to the cylinder coil, radiators, or both.
The valve position is controlled by electrical signals from the programmer and thermostats.
The Y Plan is simpler to install than S Plan+ but provides less flexibility for zoning.

## Slide 11: Y Plan schematic
Boiler and pump.
Three-port mid-position valve.
Hot water cylinder with thermostat.
Programmer/timer.
Room thermostat.
Question: What is the main limitation of the Y Plan compared to S Plan+?

## Slide 12: W Plan system
The W Plan is less common but uses a three-port diverting valve. It allows water to flow to either the hot water cylinder or the heating circuit, but not both simultaneously.
The cylinder is always prioritised; only when hot water demand is satisfied will the system divert flow to the radiators.
W Plans are often used in simpler systems where simultaneous heating and hot water is not required.

## Slide 13: W Plan features
Boiler and pump.
Three-port diverting valve.
Cylinder thermostat.
Programmer.
Prioritises hot water over heating.
Only one circuit active at a time.
Question: What common boiler type also uses a diverter valve and prioritises DHW?

## Slide 14: Comparison of S, Y, and W Plans
S Plan+ offers the most flexibility, with independent zone control. Y Plan allows heating and hot water together but only with a single mid-position valve, limiting expansion.
W Plan is the simplest but sacrifices simultaneous heating and hot water. Installers must choose the correct system based on property size, user requirements, and budget.

## Slide 15: Control principles
Programmer sets heating/hot water schedule.
Thermostats call for heat when below set temperature.
Valves open when demand is detected.
Microswitches signal boiler and pump to run.
Cylinder stat ensures hot water priority or balance.
Question: What role do valve microswitches play in control sequencing?

## Slide 16: Mid-position valve operation
In Y Plans, the three-port mid-position valve moves between hot water only, central heating only, and mid-position for both. It contains a motor and spring mechanism controlled by electrical inputs from thermostats.
In mid-position, water flows to both circuits, though heating may be reduced due to flow division.
Correct wiring is essential for proper valve function.

## Slide 17: Diverter valve operation
Used in W Plan.
Directs water to hot water or heating only.
Cylinder stat ensures DHW priority.
Simple electrical control.
No mid-position capability.
Question: How does a diverting valve differ from a mid-position valve?

## Slide 18: Tutor demonstration – schematics
The tutor should show schematic diagrams of S Plan, S Plan+, Y Plan, and W Plan systems.
Students compare layouts, noting valve types, thermostat positions, and flow directions.
Notes: Note for tutor: Examples can be found here - https://www.wolseley.co.uk/wcsstore/ExtendedSitesCatalogAssetStore/images/products/AssetPush/DTP_AssetPushHighRes/std.lang.all/ui/de/Honeywell_H_Controls_Wiring_Guide.pdf?srsltid=AfmBOoo7BiYtMf4b813cC8OQ3p44I___Qt0vuxVGTf4s_1D4d22h_KFH

## Slide 19: Student task – sketch layouts
Sketch an S Plan and S Plan+ with three two-port valves.
Sketch a Y Plan with a three-port mid-position valve.
Sketch a W Plan with a three-port diverting valve.
Label boiler, pump, valves, thermostats, and cylinder.
Notes: Tutor to provide blank templates for this task

## Slide 20: Step-by-step operation – S Plan+
When a room thermostat calls for heat, its two-port valve opens, triggering the microswitch.
The boiler and pump run, sending water to the radiators in that zone.
When the cylinder thermostat calls for hot water, the hot water valve opens and the boiler supplies the coil.
Zones can operate independently or together, providing flexibility and efficiency.

## Slide 21: Step-by-step operation – Y Plan
The programmer and cylinder thermostat call for hot water, moving the mid-position valve to cylinder-only.
If the room thermostat also calls for heat, the valve moves to mid-position, supplying both cylinder and radiators.
If only heating is needed, the valve moves fully to heating. Electrical wiring and valve position must match demand accurately.

## Slide 22: Step-by-step operation – W Plan
You would choose an S Plan for a 150m² property to allow for independent control of heating and hot water, and to easily add more heating zones in the future, which is highly beneficial for larger homes and for achieving more precise temperature management. While a Y Plan is a simpler, more compact option, it lacks the flexibility to zone heating or upgrade to more heating zones, making it less suitable for a property of this size.

## Slide 23: System selection
When the cylinder thermostat calls for heat, the diverting valve directs flow only to the cylinder. Once the hot water is satisfied, the valve diverts flow to the radiators.
The system ensures hot water has priority but cannot provide heating and hot water simultaneously.
This simplicity can be a limitation but suits smaller systems.

## Slide 24: Zoning arrangements
Zoning divides the system into separately controlled areas. In a domestic property, common zones are ground floor, first floor, and hot water.
Larger homes may have additional zones such as extensions or underfloor heating.
Each zone has its own thermostat and valve, enabling tailored heating schedules and temperatures. This approach improves efficiency and user comfort, as unused areas do not need to be heated unnecessarily.

## Slide 25: Zone control benefits
Reduces energy costs.
Improves comfort by avoiding overheating.
Allows different schedules in different areas.
Provides greater system flexibility.
Essential for compliance with modern energy standards.
Question: Why is zoning a key requirement in modern building regulations?

## Slide 26: Control principles – electrical overview
The heart of a fully pumped system is the wiring centre. Programmers send signals to thermostats, which in turn activate motorised valves. Each valve contains an end-switch that energises the boiler and pump when fully open.
This ensures water is only heated and circulated when a genuine demand exists. Correct wiring is critical; even a single misconnection can prevent the system from operating safely.

## Slide 27: Programmer functions
Sets times for heating and hot water.
Provides independent control in S Plan+.
Works with thermostats to avoid wasted heat.
May be manual, digital, or smart controlled.
Central point of system operation.
Question: What is the main difference between a programmer and a thermostat?

## Slide 28: Cylinder thermostat
The cylinder thermostat controls hot water temperature by switching the hot water valve or three-port valve. Typically set between 55°C and 65°C, it prevents both scalding and bacterial growth.
If the cylinder reaches the setpoint, the thermostat closes the circuit, shutting off heat to the coil. This prevents overheating and ensures efficiency.
Question: What is wrong with the stat in the image?

## Slide 29: Room thermostat
Monitors room temperature.
Calls for heat when temperature drops.
Signals valve and boiler via control wiring.
Can be mechanical, digital, or wireless.
Works with TRVs for balanced control (not in same room).
Question: Why is it important to position a room thermostat in a representative location?

## Slide 30: Midpoint knowledge check
How does S Plan+ achieve independent zone control?
What type of valve is used in Y Plan systems?
Why does the W Plan give hot water priority?
What is the role of a valve end-switch?
Why is zoning beneficial in large properties?

## Slide 31: Midpoint knowledge check – answers
Each zone has its own two-port motorised valve and thermostat.
A three-port mid-position valve.
Because the diverting valve always sends water to the hot water cylinder first.
It proves the valve is open and signals the boiler and pump to run.
To improve comfort, reduce wasted energy, and meet energy standards.

## Slide 32: Motorised valve components
Motorised valves consist of a small synchronous motor, gears, and a microswitch. When energised, the motor drives the valve spindle to open the port. Once open, the end-switch signals the boiler to fire.
In mid-position valves, additional wiring holds the valve halfway open for dual supply.
Understanding valve internals helps engineers diagnose electrical and mechanical faults.

## Slide 33: Operation of three-port mid-position valve
Spring returns valve to hot water position when off.
Heating demand energises motor to heating port.
Both demands energise motor and hold circuit mid-position.
Valve allows dual supply but reduces heating flow.
Complex wiring compared to S Plan+.
Question: Why does heating output sometimes reduce in mid-position mode?

## Slide 34: Operation of three-port diverting valve
Diverting valves are simpler, with only two flow options: hot water or heating. When hot water is required, the valve directs all flow to the cylinder coil.
When the cylinder stat is satisfied, the valve diverts to heating.
This simple arrangement prioritises hot water but cannot provide both circuits simultaneously, limiting flexibility.

## Slide 35: Tutor demonstration – valve operation
Show live motorised valves in training rig
Demonstrate valve opening with thermostat demand
Observe microswitch activation
Show mid-position operation
Compare diverting vs mid-position in real time

## Slide 36: Student task – valve identification
Examine cutaway valves or diagrams
Identify motor, spindle, and end-switch
Match parts to function
Discuss failure modes such as seized spindle or faulty motor

## Slide 37: Advantages of S Plan+
S Plan+ offers maximum flexibility. It allows multiple heating zones, independent control, and simultaneous hot water.
Maintenance is straightforward because each zone has its own valve, so faults can be isolated.
It also integrates well with modern controls such as smart thermostats and renewable heating systems.

## Slide 38: Advantages of Y Plan
Simple to install with fewer valves.
Provides simultaneous heating and hot water.
Well-suited to small to medium homes.
Proven reliability with common components.
Lower cost than S Plan+.
Question: Why might a Y Plan be chosen over an S Plan+ despite reduced flexibility?

## Slide 39: Advantages of W Plan
The W Plan is the simplest arrangement, using a diverting valve to prioritise hot water. It is ideal where hot water demand is more critical than heating, such as in small homes or flats.
With fewer components, it is easier to install and maintain. However, it cannot provide heating and hot water together, making it less popular today.

## Slide 40: Tutor activity – comparing plans
Show schematic diagrams of S Plan+, Y Plan, and W Plan.
Discuss advantages and disadvantages.
Highlight wiring complexity differences.
Compare zoning flexibility.
Students to choose the most suitable plan for example properties.

## Slide 41: Common faults
Typical faults include valve breakdown, failed synchron motors/microswitches, wiring errors, and thermostat malfunctions.
In S Plan+, a failed valve may prevent one zone from operating. In Y Plans, a stuck valve can lock the system in heating or hot water mode.
In W Plans, diverting valve failure may prevent either circuit from being supplied.
Fault-finding requires a clear understanding of operation sequences. Manual operation of valves can reduce disruption to the customer while a replacement component is sourced.

## Slide 42: Fault-finding tools
Multimeter for electrical continuity Safe isolation guidance - page 9
Wiring diagram for reference.
Visual inspection for leaks or seized spindles.
Functional testing of thermostats.
Manual lever check on valves.
Question: What is the first step when diagnosing a heating zone that is not operating?

## Slide 43: Step-by-step methodology task
Students should produce a written sequence of how each system operates.
For example, in S Plan+: thermostat calls → valve opens → microswitch closes → boiler and pump run → heat supplied.
Writing sequences reinforces understanding of the logical control process.

## Slide 44: Tutor demonstration – live system identification
Show installed or training rig system.
Students identify valves, pump, cylinder stat, room stat.
Trace wiring paths to programmer.
Discuss layout differences between plans.

## Slide 45: Student sketching task
Draw labelled diagrams of S Plan+, Y Plan, and W Plan.
Show flow and return pipes.
Include valves, thermostats, boiler, and cylinder.
Share sketches with peers for review.

## Slide 46: Energy efficiency considerations
Fully pumped systems save energy by directing heat only where required. Zoning and modern controls reduce wasted energy.
Condensing boilers operate more efficiently with these systems because return temperatures can be managed more effectively.
Correct system design and valve control are key to compliance with energy regulations.

## Slide 47: Integration with smart controls
Compatible with smart thermostats.
Internet-connected programmers.
Zonal scheduling via apps.
Optimisation features like weather compensation.
Enhances user convenience and efficiency.
Question: How could smart controls improve the performance of an S Plan+ system?

## Slide 48: Health and safety
When working on fully pumped systems, electrical safety is critical. Isolation must be confirmed before working on motorised valves or wiring.
Hot pipework can cause burns, so PPE should be used.
Correct discharge and expansion controls must be checked to prevent unsafe operation. Following safe systems of work ensures both installer and occupant safety.

## Slide 49: Midpoint knowledge check 2
What is the role of a cylinder thermostat?
Which plan uses three two-port valves?
Which plan uses a mid-position valve?
Why is W Plan less flexible?
What tool is essential for diagnosing electrical faults in valves?

## Slide 50: Midpoint knowledge check 2 – answers
It controls the cylinder temperature by switching the hot water circuit on/off.
S Plan+.
Y Plan.
It cannot supply hot water and heating together, only one at a time.
A multimeter or approved voltage indicating device.

## Slide 51: Student wiring task
Tutor: Present wiring diagrams for S, Y, and W Plans. Show how programmer, thermostats, and valves interact. Highlight how end-switches control boiler and pump. Students should follow signal paths to understand sequencing.
Students:
Trace control circuit on Y Plan diagram.
Identify which components energise valve motor.
Mark microswitch path to boiler and pump.
Explain sequence aloud.

## Slide 52: Troubleshooting case study
A Y Plan system fails to provide heating when hot water is satisfied.
Students must discuss issue as a group and suggest testing methods and possible causes.

## Slide 53: Student activity – compare plans
Groups compare suitability for small, medium, and large homes.
Present findings on flipchart or notes.
Tutor feedback on suitability choices.

## Slide 54: Final knowledge check
Which system is best for multiple heating zones?
Which plan cannot provide heating and hot water simultaneously?
What does a microswitch do in a valve?
Why is zoning important for energy efficiency?
Which plan uses a mid-position valve?

## Slide 55: Final knowledge check – answers
S Plan+ – because it uses multiple two-port valves for separate zones.
W Plan.
It closes the electrical circuit to fire the boiler/pump once the valve is open.
It prevents heating unoccupied areas and reduces energy consumption.
Y Plan.

## Slide 56: Demonstration – installed system walkthrough
Show boiler, pump, valves, and cylinder in working system.
Students identify live components.
Discuss operational noises (pump, valve motor).
Highlight safety and control elements.

## Slide 57: Student task – written step sequence
Write sequence for S Plan+ heating demand.
Write sequence for Y Plan hot water demand.
Write sequence for W Plan hot water priority.
Compare and peer review sequences.

## Slide 58: Energy and sustainability
Fully pumped systems with zoning reduce wasted energy. Integration with smart controls further lowers emissions.
Condensing boilers achieve highest efficiency when combined with correct valve control.
These systems help meet modern standards for sustainable energy use in housing.

## Slide 59: Summary
You should be able to:
Describe fully pumped heating systems and their operation
Explain S Plan+, Y Plan and W Plan layouts
Understand zoning and control principles
You might also be able to:
Compare diverting and mid-position valve functions
Identify components in live or schematic systems
Sketch and label system layouts

## Slide 60: Exit quiz
Which plan uses three two-port valves?
Which valve type can supply both heating and hot water together?
Why does W Plan prioritise hot water?
What is the main advantage of zoning?
Which system is most flexible for modern properties?

## Slide 61: Exit quiz – answers
S Plan+.
The Y Plan mid-position valve.
Because the diverting valve always sends water to hot water first.
Independent control and reduced wasted energy.
S Plan+ – most flexible for modern homes.

## Slide 62
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.