## Slide 1
Occupational Specialism: Protection Systems Engineering
K1.19 Making systems safe to decommission
PowerPoint 19: Making systems safe to decommission

## Slide 2: Introduction
This session looks at the safe decommissioning of protective engineering systems for fire and security applications.
We'll examine:
isolation procedures
materials handling
component removal
system reconfiguration
waste categorisation and
building fabric restoration.

## Slide 3: Objectives
By the end of this session, you should be able to:
Understand the requirements for safely isolating and de-energising fire, security, and ELV systems before decommissioning.
Understand the need for reconfiguration (e.g. temporary cover, bypassing, or zoning adjustments) to keep premises safe during the works.
Complete decommissioning tasks including:
isolation of cabling and devices
safe removal and segregation of waste equipment (batteries, electronics, cabling)
making good of building fabric and reinstating affected areas.

## Slide 4
Overview
System isolation
Safety protocols for disconnecting systems from supply sources and integrated services.
Materials handling
Techniques for maintaining integrity and
safety of components.
Component removal
Procedures for safely removing
pre-installed components.
System Reconfiguration
Methods for adapting remaining systems
during decommissioning.
Waste categorisation
Proper classification and
disposal of materials.
Building restoration
Techniques for restoring building fabric
after system removal.

## Slide 5
Risk assessment: pre-decommissioning phase
Isolation
Confirm all power supplies are identified and safely isolated.
Ensure standby batteries and PSU connections are discharged/removed.
Safety risks
Identify hazards such as live cables, working at height, dust, or asbestos.
Put in place appropriate PPE and control measures.
Documentation
Review as-fitted drawings, circuit charts, and maintenance records.
Planning for removal
Agree sequence of works and temporary measures if protection is lost.
Plan safe disposal of waste (e.g. batteries, electronic boards, cabling).

## Slide 6
Risk assessment: pre-decommissioning phase
A thorough risk assessment is the foundation of safe decommissioning.
This systematic approach identifies potential hazards and establishes mitigation measures before work begins, significantly reducing the likelihood of incidents during the process.

## Slide 7
Regulatory compliance requirements
Health and Safety at Work Act
Requires risk assessment, worker protection measures, and appropriate training for decommissioning personnel, with specific provisions for handling potentially hazardous materials.
Electricity at Work Regulations
Mandates proper isolation procedures, verification of zero energy state, and qualified personnel for electrical system decommissioning tasks.
Construction (Design and Management) Regulations
Governs planning, coordination and execution of decommissioning projects, requiring formal documentation and competent supervision.
Waste Electrical and Electronic Equipment Regulations
Specifies requirements for recycling, recovery and environmentally sound disposal of electronic components and systems.

## Slide 8
Regulatory compliance requirements
Compliance with these regulations is not merely recommended but legally mandatory.
Engineers must maintain current knowledge of these requirements and ensure all decommissioning activities adhere to the latest standards.

## Slide 9
System isolation fundamentals
Identification of supply sources
Correctly identify all energy sources connected to the system, including primary and secondary power supplies, backup systems, and external service connections that may affect or be affected by decommissioning operations.
Lockout-tagout implementation
Apply appropriate lockout-tagout devices to all energy isolation points following procedural verification. Each isolation point must be individually secured and clearly labelled with decommissioning information.
Verification of zero energy state
Use calibrated test equipment to confirm complete isolation. Test all circuits and components to verify the absence of electrical, pneumatic, hydraulic or mechanical stored energy prior to beginning work.

## Slide 10
System isolation fundamentals
Proper isolation is the critical first step in safe decommissioning.
These procedures ensure that systems cannot be accidentally energised during work, protecting both personnel and integrated building functions.

## Slide 11
Isolation of integrated services
Fire protection systems
Coordinate with responsible person to establish alternative measures before isolation:
Suppress automatic alarms to prevent false activation.
Maintain manual call points where possible.
Access control systems
Ensure emergency egress
remains functional:
Configure door releases to fail-safe positions.
Implement temporary access measures.
Security systems
Maintain critical monitoring capabilities:
Reconfigure coverage zones to compensate.
Consider temporary security measures.
Building management
systems
Prevent cascade failures in connected
systems:
Adjust control algorithms to exclude decommissioned components.
Test operational integrity after isolation.

## Slide 12
Isolation of integrated services
Integrated services often have complex interdependencies.
Proper isolation requires a thorough understanding of how these systems interact to prevent unintended consequences during decommissioning.

## Slide 13
Special considerations for emergency systems
Fire alarm modifications
When decommissioning affects fire detection zones, the entire system must be reconfigured to maintain comprehensive coverage. Temporary detection devices may be required in areas where permanent systems are removed.
Alarm verification protocols must be adjusted to prevent false negatives in modified detection areas. All modifications must be documented and communicated to emergency response teams.
Emergency lighting continuity
Maintain compliant emergency lighting throughout the decommissioning process. Temporary battery-backed lighting units may be necessary when removing sections of the permanent system.
Testing procedures must be adapted to include temporary installations. The circuit isolation must not compromise the charging capability of remaining emergency lighting units.
Evacuation route protection
Ensure all emergency exits remain functional and unobstructed. Where automated systems are decommissioned, implement manual alternatives with clear instructions for building occupants.
Update evacuation plans to reflect current system status and distribute revised instructions to all affected personnel. Consider partial or phased decommissioning to minimise impact.

## Slide 14
Materials handling: Preservation techniques
Reuse of components
Keep devices, cabling accessories, and fixings together as sets.
Package carefully to prevent damage during transport.
Label items clearly for identification (e.g. “fire panel PSU,” “door maglock”).
Safe transport
Use appropriate containers for batteries, detectors, and electronic parts.
Separate hazardous items (e.g. lead-acid batteries).
Waste disposal
Follow WEEE regulations for electronic waste.
Dispose of batteries through approved recycling channels.
Remove redundant cabling safely and recycle where possible.

## Slide 15
Materials handling: Preservation techniques
Proper materials handling ensures the integrity of components that may be:
repurposed
recycled or
analysed
for failure investigation.
These techniques preserve not only the physical condition but also the functional capabilities of decommissioned equipment.

## Slide 16
Hazardous materials: Identification and handling
Batteries and UPS systems
Contain lead-acid, lithium-ion or nickel-cadmium compounds requiring specialised handling and disposal through licensed waste handlers. Discharge protocols must be followed prior to removal to prevent fire risks.
Radioactive elements
Certain smoke detectors contain americium-241. These must be identified, segregated, and processed through authorised radioactive waste channels with proper documentation.
Mercury switches and sensors
Found in older tilt sensors and float switches. Handle in sealed containers to prevent vapour release and dispose through chemical waste specialists with full chain-of-custody documentation.

## Slide 17
Hazardous materials: Identification and handling
A thorough hazardous materials assessment must take place before starting any decommissioning activity.
Personnel must be properly trained and equipped with appropriate PPE specific to the materials present in the system.

## Slide 18
Document type
Required content
Format
Retention period
Component
Inventory
Serial numbers, manufacturer, installation date, hazardous material content
Electronic and
hardcopy
Decommissioning
Plan
Step-by-step procedures, risk assessments, required tools and equipment
Controlled document with approvals
Component
Labels
Unique ID, removal date, hazard information, handling instructions
Durable, weather-resistant tags
Until final
disposal
Waste Transfer
Notes
Material classification, quantities, destination facility
Legal
documentation
Documentation and labelling requirements
Until final
disposal
Until final
disposal
Until final
disposal

## Slide 19
Documentation and labelling requirements
Comprehensive documentation provides traceability throughout the decommissioning process.
It ensures regulatory compliance and facilitates proper handling of materials from removal through to final disposal or repurposing.

## Slide 20
Component removal: Sequential approach
User interface components
Control panels, displays, and input devices
Field devices
Sensors, detectors, and peripheral equipment
3
Control modules
Processing units and system controllers
Distribution network
Cabling, conduits, and connection points
Power supply infrastructure
Transformers, batteries, and primary connections

## Slide 21
Component removal: Sequential approach
This top-down approach to component removal ensures that dependent systems are decommissioned before their supporting infrastructure.
Starting with user interfaces and working down to power supplies minimises the risk of accidental system activation and prevents damage to sensitive components.
Each stage must be fully completed and verified before proceeding to the next. This methodical process allows for system verification and troubleshooting at each step, reducing the complexity of identifying issues during decommissioning.

## Slide 22
Specialised tools and equipment
Using the correct tools is essential for both safety and efficiency during decommissioning.
All equipment must be properly calibrated, tested and certified before use, and used correctly.
Specialised tools should be selected based on the specific systems being decommissioned and the potential hazards present.
Equipment should be inspected before each use to ensure it remains in good working condition throughout the decommissioning process.

## Slide 23
System verification during component removal
Safe isolation
Confirm all power (mains and standby) is safely disconnected.
Remove or safely isolate batteries/PSUs.
No adverse impact
Check that removing components hasn’t affected connected systems.
Reconfigure or bypass as needed to keep retained systems operational.
Confirm functionality of retained systems
Test key devices and system functions that remain
in service.
Record checks in the logbook and update system
documentation.

## Slide 24
System verification during component removal
When decommissioning fire and security systems, system verification should remain practical and focused on safety.
The first priority is always safe isolation. This means confirming that mains supplies have been disconnected, standby batteries or PSUs have been removed or made safe, and no live circuits remain that could pose a risk during the removal works.
Once isolation is complete, make sure the removal of a component does not cause unintended problems elsewhere. Many systems share loops, zones, or signalling paths, so check for dependencies and reconfigure or bypass circuits where necessary to keep retained systems operational.

## Slide 25
System verification during component removal
Finally, a basic check of any retained systems should be carried out, e.g. confirming that fire detection devices still activate correctly, intruder zones still set and unset, or CCTV continues to record. These checks, along with updates to the logbook and system documentation, provide assurance that the system remains safe and functional after decommissioning activity.

## Slide 26
Handling of sensitive and fragile components
General care
Handle detectors, sounders, panels, and other devices carefully to avoid unnecessary damage.
Packaging and transport
Bag or box items together to keep components safe and organised.
Use suitable containers for batteries or electronic parts (follow WEEE and recycling requirements).
Reuse or specialist disposal
Label any items being retained for reuse clearly.
Dispose of redundant or damaged items through approved recycling or waste channels.

## Slide 27
Handling of sensitive and fragile components
Each component type requires specific handling techniques based on its construction and vulnerabilities.
Damage during removal can not only impact potential reuse but may also create additional hazards for handling personnel.

## Slide 28
Reconfiguration of remaining systems
Assess impact
Determine how removed components affect remaining system functionality and identify required compensatory measures
Develop new configuration
Design a modified system architecture that maintains the required functionality with available components
Implement changes
Apply reconfiguration through hardware adjustments, software updates, and controller reprogramming
Verify operation
Test new configuration under various scenarios to confirm reliability and performance

## Slide 29
Reconfiguration of remaining systems
Reconfiguration ensures that partial decommissioning doesn't compromise the functionality of interdependent systems that must remain operational. This process requires deep understanding of both the systems being removed and those that will continue to function.
Documentation must be updated to reflect the new configuration, including revised schematics, updated programming, and modified operating procedures for maintenance personnel and end users.

## Slide 30
Maintaining system integrity during transition
Temporary protective measures
Implement interim solutions to maintain critical functions while permanent systems are being decommissioned. This may include portable detection units, temporary power arrangements, or manual monitoring procedures.
Enhanced communication protocols
Establish clear reporting chains for system status during transitional periods. All stakeholders must be aware of current protection capabilities and any temporary limitations during the decommissioning process.
Phased implementation schedule
Coordinate decommissioning activities to minimise vulnerability periods. Schedule critical work during low-risk timeframes and ensure adequate resources for rapid system restoration if required.
Increased verification frequency
Implement additional testing and monitoring during transition periods. Verify system performance after each significant modification to quickly identify and address any emergent issues.

## Slide 31
Maintaining system integrity during transition
The transition period during decommissioning presents unique vulnerabilities that must be actively managed.
A comprehensive transition plan ensures continuous protection even as systems undergo significant changes.

## Slide 32
Electronic waste management
Classification requirements
Under the WEEE Directive, electronic components must be categorised by type (IT equipment, monitoring/control instruments, etc.), hazardous content, and recyclability. This classification determines the appropriate recycling or disposal route.
Data security considerations
Storage devices and components containing configuration data must undergo secure data erasure or physical destruction before disposal. Documentation of data sanitisation is required for compliance with data protection regulations.
Producer responsibility schemes
Many manufacturers offer take-back programmes for their equipment. These schemes often provide the most environmentally sound disposal route and may offset disposal costs through partial credit for newer equipment.
Documentation requirements
Maintain complete chain of custody records for all electronic waste. Waste Transfer Notes must include EWC codes, quantities, and destination facilities. Retain evidence of appropriate license holders for all stages of handling.

## Slide 33
Electronic waste management
Electronic waste represents both an environmental risk and a potential source of value.
Proper management ensures hazardous elements are contained while recoverable materials are directed to appropriate recycling streams.

## Slide 34
Hazardous waste handling protocols
Identification and segregation
Hazardous components must be identified through documentation review, visual inspection, and when necessary, laboratory testing. Segregate materials by hazard class to prevent incompatible materials from contacting during storage and transport.
Specialised containment
Use UN-approved containers appropriate for the specific hazard class. Double containment may be required for liquids and materials with leaching potential. All containers must be properly labeled with hazard diamonds and material identification.
Qualified transportation
Only licensed hazardous waste carriers may transport these materials. Vehicles must meet ADR requirements with appropriate placarding. Consignment notes must accompany all shipments with detailed hazard information.
Cradle-to-grave documentation
Maintain comprehensive records from generation through final disposal. Consignment notes must be retained for at least 3 years. Treatment facilities must provide verification of appropriate processing methods.

## Slide 35
Hazardous waste handling protocols
Hazardous waste management carries significant legal and environmental responsibilities.
Improper handling can result in substantial penalties, environmental damage, and reputational harm.

## Slide 36
Material recovery and recycling opportunities
99%
Copper recovery rate
From properly sorted wiring and components
95%
Aluminium recycling
From enclosures and heat sinks
85%
Circuit board reclamation
Recovery of precious metals including gold, silver and palladium
£120/kg
Average value
For recovered precious metals from high-grade circuit boards

## Slide 37
Material recovery and recycling opportunities
Material recovery represents both environmental benefit and potential cost offset for decommissioning projects.
Proper segregation significantly increases the value of recoverable materials.
Specialised recycling facilities can extract precious metals from circuit boards, including gold, silver, palladium, and platinum used in connectors and components.
Establishing relationships with certified recyclers ensures that materials are properly processed while maximising recovery value. This approach supports circular economy principles and reduces the environmental footprint of decommissioning activities.

## Slide 38
Building fabric restoration techniques
Essential fire-stopping
Seal all penetrations to maintain compartmentation.
Use approved fire-rated materials (sealant, pillows, grommets).
Basic making-good
Fill holes and leave the area safe and tidy.
Reinstate covers, blanking plates, or basic finishes as needed.
Aesthetic / structural restoration
Full finish matching (e.g. brickwork, plaster, paint) is usually outside the scope.
Extent of work depends on the contract agreement and the client’s responsibility.

## Slide 39
Building fabric restoration techniques
Building fabric restoration must maintain:
structural integrity
fire safety compliance
aesthetic continuity.
Documentation of restored fire barriers is particularly important for building certification and insurance requirements.

## Slide 40
Case study: office building fire system decommissioning
Original Timeline (Days)
Actual Timeline (Days)
Notes: This 10-storey office building required decommissioning of an obsolete fire detection system while maintaining continuous protection. The project implemented a phased approach, with temporary detection measures deployed as zones were decommissioned. Planning took longer than anticipated due to discovering undocumented system integrations with the HVAC and access control systems.
Component removal proceeded more efficiently than expected due to well-documented system architecture. However, waste management and restoration phases extended beyond projections due to discovering asbestos-containing materials in some wall penetrations that required specialist handling.

## Slide 41
Best practices for successful decommissioning
Comprehensive documentation
Review
Invest significant time in reviewing all available system documentation before beginning physical work. Identify and resolve documentation gaps through site surveys and stakeholder interviews to prevent surprises during the decommissioning process.
Stakeholder engagement
Involve all affected parties in planning, including facilities management, security personnel, and building users. Clear communication about timeframes, temporary measures, and expected impacts ensures cooperation and minimises disruption.
Continuous risk assessment
Treat risk assessment as an ongoing activity throughout the project, not just an initial planning step. Regular reviews of changing conditions and newly identified hazards allow for adaptive mitigation measures.
Verification at every stage
Implement systematic testing and verification after each significant activity. This incremental approach allows immediate identification and correction of issues before they compound into larger problems.

## Slide 42
Best practices for successful decommissioning
These best practices have been derived from an analysis of hundreds of successful decommissioning projects across various industries.
Their consistent application significantly reduces the likelihood of safety incidents, regulatory non-compliance, and project delays.

## Slide 43: Summary
Safety is paramount
All procedures must prioritise personnel and building safety
Thorough planning prevents problems
Comprehensive documentation and risk assessment are essential
Systems integration understanding is critical
Identify all dependencies before beginning physical work
Regulatory compliance must be maintained
Follow all applicable standards throughout the process
Documentation creates lasting value
Complete records protect against future liability

## Slide 44: Summary
You should now be able to:
Understand the requirements for safely isolating and de-energising fire, security, and ELV systems before decommissioning.
Understand the need for reconfiguration (e.g. temporary cover, bypassing, or zoning adjustments) to keep premises safe during the works.
Complete decommissioning tasks including:
isolation of cabling and devices
safe removal and segregation of waste equipment (batteries, electronics, cabling)
making good of building fabric and reinstating affected areas.

## Slide 45
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.