## Slide 1
Occupational Specialism: Protection Systems Engineering
K1.5 Types of protection systems, signalling and notification
PowerPoint 1.5: Types of protection systems, signalling and notification

## Slide 2: Introduction
This session we're diving into the world of building protection systems - how different systems help keep buildings safe, from fire alarms to emergency lighting.
How fire detection systems work (smoke, heat, and manual call points).
Basics of access control, CCTV, and intruder alarms.
Why emergency lighting is important during power cuts or evacuations.
The difference between conventional and addressable systems.
Key rules from British Standards that guide how these systems are installed and tested.
These systems are part of the critical infrastructure that protects people and property. Whether you're installing, testing, or maintaining them, understanding how they work is essential for your role in building services engineering.

## Slide 3: Objectives
By the end of this session, you should be able to:
Understand the types of protection systems used in the industry.
Understand signalling and notification types used in protection systems.
Understand basic transmission methods in protection systems.

## Slide 4
Overview
Fire detection systems
Conventional and addressable systems for early
detection and warning.
Access control systems
Solutions for managing and restricting building entry and exit.
Video surveillance
CCTV technologies for monitoring and recording activities.
Intruder & hold up alarms
Systems for detecting unauthorised entry and duress situations.

## Slide 5
Overview
Protection systems form the backbone of building security infrastructure.
Each system serves a specific purpose but works in concert with others to create a comprehensive protection strategy.
These systems vary in complexity from basic conventional installations to sophisticated addressable networks.

## Slide 6
Fire detection systems: conventional vs addressable
Conventional systems
Organised into zones where multiple devices trigger the same zone alarm. Cost-effective for smaller premises but provides less precise location information.
Zone-based identification
Simpler wiring and configuration
Lower initial cost
Suitable for smaller installations
Addressable systems
Each device has a unique address, allowing precise identification of the activated detector or call point. Offers enhanced control and monitoring capabilities.
Individual device identification
Detailed status monitoring
Pre-alarm warnings
Reduced false alarms
Both systems must comply with BS 5839 standards, with system choice typically determined by building size, complexity, and risk assessment outcomes.

## Slide 7
Fire detection system components
Detection devices
Smoke, heat, multi-sensor, and flame detectors that respond to fire signatures
Alarm devices
Sounders, beacons, and voice alarm systems for evacuation notification
Control equipment
Control panels, power supplies, and interface modules
Network infrastructure
Cabling, network cards, and communication pathways

## Slide 8
Fire detection system components
Fire detection systems comprise an interconnected network of devices that work together to detect fires, alert occupants, and initiate predefined responses.
System components must be selected based on environmental conditions, building usage, and fire risk assessment outcomes.

## Slide 9
British standards for fire detection
BS 5839-1
Covers fire detection and alarm systems in non-domestic premises. Defines system categories (L1-L5 for life protection, P1-P2 for property protection) and provides guidance on design, installation, commissioning, and maintenance.
BS 5839-6
Focuses on fire detection and alarm systems in domestic premises. Establishes grades of system (A-F) and categories (LD1-LD3) based on level of protection required.
BS EN 54 Series
Component standards specifying requirements for individual system elements such as detectors, control equipment, and alarm devices. Ensures compatibility and performance standards.
Compliance with British Standards is essential for legal operation and insurance validity. Systems must be designed, installed, and maintained according to these standards, with appropriate documentation provided throughout the system lifecycle.

## Slide 10
Access control systems
Credential types
Cards, fobs, biometrics, PINs, mobile credentials
Entry points
Readers, electric locks, turnstiles, barriers
Control systems
Controllers, software, databases
Integration
Fire, CCTV, HR, visitor management

## Slide 11
Access control systems
Access control systems regulate who can enter specific areas of a building, when they can enter, and under what conditions.
Modern systems offer granular control over permission levels, time-based access, anti-passback features, and detailed audit trails of all entry and exit events.

## Slide 12
Access control standards and guidelines
BS EN 60839-11-1
Electronic access control systems - System and components requirements
BS EN 60839-11-2
Electronic access control systems - Application guidelines
BS EN 50133
Alarm systems - Access control systems for security applications
BS 7273-4
Code of practice for the operation of fire protection measures - Part 4: Actuation of release mechanisms for doors
SIA ANSI/BHMA A156.25
Electrified locking devices standards

## Slide 13
Access control standards and guidelines
Compliance with these standards ensures access control systems meet minimum performance requirements and integrate correctly with other building systems, particularly fire safety systems.
Requirements include fail-safe operation during emergencies and appropriate monitoring capabilities.

## Slide 14
Video surveillance systems (CCTV)
Monitoring and storage
VMS software, NVRs, cloud storage
Transmission
IP networks, wireless, encoders
Capture devices
IP cameras, analogue cameras, specialty cameras

## Slide 15
Video surveillance systems (CCTV)
Modern video surveillance systems have evolved dramatically from simple analogue circuits to sophisticated IP-based networks.
Today's systems offer high-definition imagery, intelligent video analytics, and extensive integration possibilities with other protection systems.
Camera selection should be based on specific area requirements, including lighting conditions, field of view needs, and environmental considerations.
Network infrastructure must be designed to handle the bandwidth demands of video transmission.

## Slide 16
CCTV camera types and applications
Fixed cameras
Dome cameras - discreet monitoring
Bullet cameras - visible deterrent
Box cameras - customisable lens options
Best for consistent viewing of specific areas
PTZ cameras
Pan, tilt, zoom capabilities
Operator or preset movement patterns
Up to 360° coverage
Ideal for large area monitoring
Specialty cameras
Thermal cameras for heat detection
Low-light cameras for night vision
Explosion-proof for hazardous areas
Multi-sensor for 180/360° coverage

## Slide 17
CCTV camera types and applications
Camera selection should be driven by specific operational requirements and environmental conditions.
Modern systems typically employ a mixture of camera types to achieve comprehensive coverage while controlling costs.

## Slide 18
Video surveillance standards
BS EN 62676 Series
Video surveillance system requirements, covering system design, components, transmission protocols, and applications.
ICO CCTV Code of Practice
Data protection guidelines for responsible use of surveillance systems, ensuring compliance with GDPR.
BS 7958
Management and operation of CCTV control rooms, addressing operational procedures and staff requirements.
BS 8418
Installation and remote monitoring of detector-activated CCTV systems, specifying requirements for remotely monitored systems.

## Slide 19
Video surveillance standards
In addition to technical standards, CCTV systems must comply with privacy legislation (GDPR) and follow the Surveillance Camera Code of Practice.
Proper signage must inform people they are being monitored, and recorded footage must be securely stored and managed.

## Slide 20
Intruder and Hold Up Alarm Systems (I&HAS)
Detection devices
PIR sensors, door/window contacts, glass break detectors
Control equipment
Panels, keypads, tag readers, smartphone apps
Signalling devices
Bells, strobes, communicators
Transmission systems
GSM, IP, radio

## Slide 21
Intruder and Hold Up Alarm Systems (I&HAS)
Intruder alarm systems detect unauthorised entry and provide local and/or remote notification. Hold up alarms allow for discreet activation during duress situations.
Systems range from simple standalone installations to complex integrated networks with multiple layers of protection.

## Slide 22
I&HAS Grades and Standards
4
Security grades
BS EN 50131 defines security grades from 1 (low risk) to 4 (high risk)
2
Environmental classes
Class I (indoor) to Class IV (outdoor, extreme conditions)
6
ATS categories
Alarm Transmission System categories defining reliability and security

## Slide 23
I&HAS Grades and Standards
Insurance companies often specify minimum security grades for policy compliance, particularly for commercial premises or high-value residential properties.

## Slide 24
Intruder detection technologies
Motion detection
Passive infrared (PIR), microwave, and dual technology sensors detect movement within protected areas through thermal changes or Doppler effect.
Perimeter protection
Magnetic contacts, vibration sensors, and acoustic glass break detectors monitor building openings and boundary integrity.
Space protection
Photoelectric beams, pressure mats, and trapped area detectors create invisible barriers or monitored zones.
Visual verification
Video motion detection and image verification cameras combine detection with visual confirmation.

## Slide 25
Intruder detection technologies
Effective intruder detection requires layered protection with complementary technologies.
System design should include a mix of perimeter, space, and point protection to create defence in depth.

## Slide 26
Hold up alarm systems
Fixed buttons
Mounted under counters, desks, or in secure locations. Provide immediate silent alarm activation during duress situations. Must be positioned to avoid accidental activation while remaining easily accessible when needed.
Portable devices
Wireless pendants, wristbands, or key fobs allow staff to summon help from anywhere within radio range. Critical for vulnerable workers or those who move throughout a facility. Require regular testing and battery maintenance.
Code entry systems
Special duress codes entered into standard keypads trigger silent alarms. Useful as a secondary option when traditional buttons cannot be reached. Staff training essential to ensure proper use during high-stress situations.
Hold up systems must comply with BS EN 50131-2-6 and connected directly to police-registered ARCs. Unlike intruder alarms, hold up systems are designed for activation during an incident, not preventative detection, making reliability and immediate response critical.

## Slide 27
Addressable emergency lighting systems
Central monitoring
Addressable systems continuously monitor each emergency light's status, battery condition, and lamp functionality through dedicated control panels or building management integration.
Individual addressing
Each emergency luminaire has a unique digital address, allowing precise identification of specific unit status and fault conditions. This enables targeted maintenance and reduces system downtime.
Automated testing
Systems conduct programmed functional and duration tests as required by BS 5266, with results automatically logged for compliance records. This eliminates manual testing requirements and ensures consistent verification.

## Slide 28
Addressable emergency lighting systems
Addressable emergency lighting represents a significant advancement over conventional systems, offering improved reliability, reduced maintenance costs, and comprehensive compliance documentation.
These systems integrate with other building services through standard protocols or proprietary interfaces.

## Slide 29
Emergency lighting standards
BS 5266-1
Code of practice for emergency lighting of premises
BS EN 1838
Lighting applications - Emergency lighting
BS EN 60598-2-22
Luminaires for emergency lighting
BS EN 50172
Emergency escape lighting systems
BS 7671
Requirements for electrical installations (IET Wiring Regulations)

## Slide 30
Emergency lighting standards
Emergency lighting systems must undergo monthly functional tests and annual full duration tests (typically 3-hours), with results documented in a logbook.
Addressable systems automate this process, maintaining electronic records and generating compliance reports.
Different categories of emergency lighting (escape route, open area, high-risk task area) have specific illumination requirements defined in the standards.

## Slide 31
System voltage levels
Extra-low voltage (ELV)
Typically, 12V or 24V DC systems
Access control readers
Most intruder alarm components
CCTV cameras (PoE)
Self-contained emergency lighting
Low Voltage (LV)
230V AC systems
Centralised emergency lighting
Fire alarm systems
Electric locking (mag locks, strikes)
Powered gates and barriers
Lower risk of electric shock but susceptible to voltage drop over distance.
Higher power capacity but requires qualified electricians for installation.

## Slide 32
Signalling and notification overview
Local
notification
On-site audible and
visual alarms
Building
management
Integration with
BMS/BEMS
Private
signalling
Direct notification to
stakeholders
Remote
monitoring
ARC and emergency
services

## Slide 33
Signalling and notification overview
Effective protection systems rely on appropriate signalling and notification strategies to alert occupants, building managers, and emergency responders.
Different systems require specific notification approaches based on risk assessment, regulatory requirements, and operational needs.
Signal path redundancy is increasingly important, with modern systems using multiple communication technologies to ensure reliable alarm transmission.

## Slide 34
Local audible and visual signalling
Audible devices
Bells, electronic sounders, and voice alarm systems provide audible notification of alarm conditions. Sound levels typically 65dBA at bedhead or 75dBA minimum throughout occupied areas per relevant standards. External bells for intruder alarms can output 115dB
Visual indicators
Strobes, beacons, and LED indicators provide visual notification, especially for hearing-impaired occupants or high-noise environments. Flash rates and illumination levels specified in standards.
Voice notification
Sophisticated emergency voice communication systems deliver specific instructions beyond simple alarm tones. Intelligibility requirements defined in BS 5839-8 ensure message clarity.

## Slide 35
Local audible and visual signalling
Local signalling devices must be selected based on building acoustics, occupant characteristics, and ambient conditions.
Different systems (fire, security, etc.) require distinct audible signatures to avoid confusion during emergencies.

## Slide 36
Visual alarm device requirements
BS EN 54-23 categories
Category C: Ceiling mounted (coverage defined by diameter)
Category W: Wall mounted (coverage defined by square dimensions)
Category O: Open class with manufacturer-defined coverage
Defined by specific coverage volume and mounting height
Performance requirements
Minimum light output of 0.4 lux throughout coverage area
Flash rate between 0.5Hz and 2Hz (typically 1Hz)
Red or white light (red standard for fire systems)
Synchronisation between devices in same field of view
Application considerations
Required in high noise areas (>90dBA)
Needed for hearing-impaired occupants
Specific requirements for sleeping accommodations
Current draw considerations for system design
Visual alarm devices play a crucial role in inclusive alarm system design, ensuring that notifications reach all building occupants, regardless of their hearing ability or environmental conditions. Proper placement requires consideration of obstructions, ambient lighting, and viewing angles.

## Slide 37
Remote signalling: Alarm receiving centres
Signal generation
Alarm transmission equipment at protected premises
Transmission path
Communication networks between premises and ARC
Signal reception
ARC equipment and monitoring software
Response protocol
Verification and emergency service dispatch

## Slide 38
Remote signalling: Alarm receiving centres
Remote signalling requirements and system grading
Remote signalling allows intruder and hold-up alarm systems to communicate alarm conditions to an Alarm Receiving Centre (ARC).
The level of signalling performance required depends on the grade of the system, which is based on risk and insurance requirements.
Key points:
Grades (1–4) define the resilience of the overall alarm system (EN 50131).
Alarm Transmission System (ATS) requirements are set by BS EN 50136.
Higher grades = stronger signalling paths, redundancy, and monitoring.
Selection depends on premises risk, insurer requirements, and police response criteria.

## Slide 39
Alarm Transmission System (ATS) categories
ATS Category
Primary Path
Secondary Path
Polling Frequency
Typical Applications
ATS 1
PSTN
None
24 hours
Low-risk domestic
ATS 2
PSTN
None
25 minutes
Low-risk commercial
ATS 3
IP/GPRS
Optional
3 minutes
Medium-risk commercial
ATS 4
IP
GPRS
90 seconds
High-risk commercial
ATS 5
IP
GPRS/RF
30 seconds
Banks, high-value
ATS 6
IP
IP+GPRS
10 seconds
Critical infrastructure

## Slide 40
Alarm Transmission System (ATS) categories
Alarm Transmission Systems must comply with BS EN 50136, which defines requirements for reliability, security, and performance.
Higher ATS categories provide increased supervision, faster fault reporting, and greater resistance to substitution attacks.

## Slide 41
Remote signalling: Alarm receiving centres
Remote signalling requirements and system categories (Fire)
Remote signalling ensures that fire alarm activations are automatically transmitted to an Alarm Receiving Centre (ARC) or directly to the Fire and Rescue Service (FRS).
Requirements depend on the system category and the risk profile of the premises.
Key points:
Remote signalling is covered under BS EN 54-21 (alarm transmission) and referenced in BS 5839-1
Signalling is required where there is:
  Sleeping risk (e.g. hotels, care homes, HMOs)
  Unoccupied or low-occupancy periods
  Insurer / enforcing authority requirements.
Transmission paths should be secure, fault-monitored, and capable of sending both fire and fault conditions.

## Slide 42
Remote signalling: Alarm receiving centres
System category | Application / risk | Remote signalling requirement | Example methods
M (Manual) | Occupants raise alarm only | Generally no remote signalling required unless insurer specifies | None, or optional link to ARC
L4 / L3 (Life) | Escape routes & adjoining areas | Recommended where building is unoccupied or has sleeping risk | Digital communicator, IP, GSM
L2 / L1 (Life) | High-risk areas / all areas covered | Strongly recommended – ensures 24/7 coverage and rapid FRS response | Dual-path IP + cellular, ARC monitored
P2 (Property) | Specific high-value/asset areas | ARC signalling required to protect assets, especially outside hours | DualCom, Emizon, IP-based ATS
P1 (Property) | Maximum protection across entire premises | Mandatory remote signalling to ARC/FRS with high resilience | Dual path, monitored ATS, EN-compliant fire transmission

## Slide 43
Private signalling methods
Speech diallers
Electronic devices that connect to alarm systems and call pre-programmed telephone numbers when triggered. They play recorded voice messages informing recipients of the alarm condition. Limited to 10 numbers under UK regulations and cannot dial emergency services directly.
Mobile applications
Smartphone apps connected to modern alarm systems provide instant push notifications with alarm details. Many offer remote viewing of connected cameras, system control capabilities, and activity logs. Require internet connectivity at both the protected premises and user device.
SMS notifications
GSM communicators that send text messages to multiple recipients when alarms activate. Simple, reliable technology that works where mobile coverage exists. Suitable for basic notification but offers limited information and no interactive capabilities.

## Slide 44
Private signalling methods
Private signalling methods complement professional monitoring services, providing immediate notification to stakeholders.
These methods should not replace ARC monitoring for high-security applications but can enhance overall communication strategies.

## Slide 45
System integration and interfaces
Modern protection systems use integration strategies to enhance functionality and operational efficiency.
Common interfaces include fire alarms releasing access-controlled doors, CCTV providing visual verification of alarm activations, and centralised monitoring through building management systems.
Integration methods range from simple volt-free contacts and relay interfaces to sophisticated digital protocols and API connections. All integrations must maintain system integrity and comply with relevant standards for each subsystem.

## Slide 46
Security risk assessment
Identification
Identify assets, threats,
and vulnerabilities
Analysis
Evaluate likelihood and impact of security breaches
Mitigation
Determine appropriate
protection measures
Documentation
Produce comprehensive
security plan

## Slide 47
Security risk assessment
This forms the foundation for the design of protection systems.
The process follows established methodologies defined in standards such as BS EN 62676-4 (CCTV), BS EN 50131-7 (intruder alarms), and BS EN 60839 (access control).
Assessments should be reviewed regularly and after significant incidents or changes to the building or its usage.
Documentation serves both as design guidance and evidence of due diligence.

## Slide 48
Protection system selection for different building types
Protection system selection must reflect the specific risks, regulatory requirements, and operational needs of each building type. System complexity generally increases with risk level, value of assets protected, and regulatory mandates.
Building type | Fire detection | Intruder alarm | Access control | CCTV
Small Business | Conventional system (basic detectors, manual call points) | Grade 2 system, confirming technology to reduce false alarms | Standalone keypad or basic network | 4–8 cameras with local recorder (NVR)
Retail | Addressable system (devices individually identified) | Grade 2/3 system, optional panic alarm | Controls for staff areas and loading bays | Wider coverage, video analytics
Critical Infrastructure | Multi-sensor detection and aspirating smoke detection (ASD) | Grade 4 system, layered protection | Multi-factor authentication, mantrap entry systems | Full site coverage, 24/7 monitoring with redundancy

## Slide 49
Protection system implementation process
Need identification and risk assessment
Conduct a thorough evaluation of risks, regulatory requirements, and operational needs. Engage stakeholders to understand specific concerns and objectives. Document findings in a formal risk assessment report.
System design and specification
Develop detailed design documentation including equipment specifications, layout drawings, cable schedules, and functionality matrices. Ensure compliance with relevant standards and create comprehensive quotation.
Installation and commissioning
Implement systems according to design documentation, with regular quality checks and interim testing. Commission system with thorough verification of all functions and integration points. Complete required documentation.
Handover and maintenance
Provide user training, operational documentation, and compliance certificates. Establish a regular maintenance schedule in accordance with applicable standards. Review system performance periodically.

## Slide 50
Protection system implementation process
Successful implementation requires careful project management with clear documentation at every stage.
Commissioning procedures must verify both the operation of individual components and the integrated system's functionality.

## Slide 51
Regulatory framework for protection systems
Building regulations
Approved Document B (Fire Safety)
Approved Document Q (Security)
Fire safety legislation
Regulatory Reform (Fire Safety) Order
Fire Safety Act 2021
Security requirements
Insurance specifications
Secured by Design
Privacy and Data Protection
GDPR and UK Data Protection Act
CCTV Code of Practice
Protection systems must comply with a complex framework of regulations, codes, and standards. Building Regulations set minimum requirements for fire safety and security in new buildings and significant refurbishments. The Regulatory Reform (Fire Safety) Order places ongoing responsibility on the "responsible person" to maintain fire safety.

## Slide 52
Industry certification bodies
BAFE (British Approvals for Fire Equipment)
Primary certification body for fire protection companies. Schemes cover design, installation, commissioning, and maintenance of fire systems. SP203 scheme specifically addresses fire detection and alarm systems.
NSI (National Security Inspectorate)
Certifies companies for security and fire systems. Gold and Silver schemes assess technical capability and management systems. Required for police response to intruder alarms and access to many insurance markets.
SSAIB (Security Systems & Alarms Inspection Board)
Certification for security system installers and monitoring centres. Focuses on smaller and medium-sized companies. Certification schemes cover intruder alarms, CCTV, access control, and fire systems.

## Slide 53
Industry certification bodies
These certification bodies provide third-party verification that companies meet relevant standards and possess the technical capabilities required for professional system installation and maintenance.
Certification typically involves initial assessment, ongoing surveillance audits, and regular technical inspections.

## Slide 54
Documentation requirements
Comprehensive documentation is essential for protection systems throughout their lifecycle. British Standards specify minimum documentation requirements for each system type, covering design rationale, installation details, commissioning results, and ongoing maintenance activities.
Fire systems - records must be maintained in a logbook as required by the Regulatory Reform (Fire Safety) Order.
Intruder alarms - require documentation of all false alarm causes and remedial actions.
Documentation forms crucial evidence of compliance with regulatory requirements and due diligence.

## Slide 55: Summary
You should now be able to:
Understand the types of protection systems used in the industry.
Understand signalling and notification types used in protection systems.
Understand basic transmission methods in protection systems.

## Slide 56
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.