## Slide 1
Occupational Specialism: Protection Systems Engineering
K1.7 Protection System Circuits
PowerPoint 1.7: Protection system circuits

## Slide 2: Introduction
In this session, we'll explore the various types of circuits used in protection systems, their properties, applications, advantages, and limitations.
We'll examine everything from traditional open and closed loops to modern addressable systems and wireless technologies.
By the end, you'll have a thorough understanding of how these circuits function, their ideal applications, and the technical considerations necessary for optimal implementation in protection engineering systems.

## Slide 3: Objectives
By the end of this session, you should be able to:
Understand protection system circuit configurations.
Interpret protection system wiring schematics.
Check and verify basic circuit continuity and functionality.

## Slide 4
Overview
Circuit types and topologies
Explore various protection system circuits and their structures.
Technical properties
Analyse suitability, applications, advantages and limitations.
Data communication
Understand bus topologies and connection methods.
Electrical considerations
Examine resistance effects and voltage drop implications.

## Slide 5
Wiring topologies
Topologies in protection systems refer to the way devices like detectors, alarms, and control panels are connected together.
The layout of these connections affects how signals travel, how faults are detected, and how easy the system is to install and maintain.
Common topologies include radial, loop, and star configurations. Each has its own advantages depending on the size of the system, the type of building, and the level of fault tolerance required.
Understanding these layouts helps you to design and troubleshoot systems more effectively.
Notes: A pictorial example can be found at - https://www.ibm.com/think/topics/network-topology

## Slide 6
Radial circuit
Design principles
Radial circuits feature unidirectional signal flow without feedback. They operate on the principle that when the loop is interrupted, the control panel detects the change in circuit parameters and triggers an alarm condition.
Applications
Commonly used in basic fire alarm systems, perimeter security, and simple intrusion detection applications. Well-suited for smaller installations where cost-effectiveness is prioritised over sophisticated monitoring capabilities.
Limitations
Traditional radial circuits offer limited fault detection and can't pinpoint device locations, making them prone to tampering and false alarms. However, newer systems use resistors to help identify fault locations, allowing quicker and more accurate responses from users and technicians.

## Slide 7
Loop circuit
Design principles
Loop configurations connect devices in a continuous ring, allowing signals to travel in both directions. This design improves fault tolerance because if one part of the loop is damaged, communication can still continue from the other side.
Applications
Loop systems are commonly used in addressable fire alarm systems and large buildings where reliability and device monitoring are important. They support a high number of devices and allow for detailed fault reporting.
Limitations
Loop configurations can be more complex to install and program. If both ends of the loop are broken, the system may lose communication with all devices. They also require careful planning to avoid wiring errors.

## Slide 8
Star circuit
Design principles
Star configurations connect each device directly to the control panel using individual cables. This layout is simple and makes it easy to identify and isolate faults, as each cable only affects one device.
Applications
Star systems are often used in smaller installations such as access control, CCTV, and basic fire alarm systems. They are ideal where fewer devices are needed, and simplicity is preferred.
Limitations
Star configurations require more cabling, which can increase installation time and cost. If a cable is damaged, the connected device will stop working until the cable is repaired or replaced.

## Slide 9
Circuit configuration
Circuit configurations in protection systems refer to the wiring arrangement of devices such as detectors, call points, and sounders.
These configurations affect how the system detects faults and responds to alarms.
Common types include open and closed circuits, as well as monitored setups using techniques like End-of-Line (EOL) resistors and Fully Supervised Loop (FSL) wiring.
Closed circuits are normally complete and trigger an alarm when broken, while open circuits are normally incomplete and activate when closed.
EOL and FSL methods help monitor the health of the wiring and detect issues such as short circuits or cable damage, improving system reliability and safety.

## Slide 10
Normally closed (NC) circuit
Operating principle
NC circuits maintain a continuous flow of current during normal operation. An alarm condition is triggered when the loop is broken, disturbing the steady-state current flow. This 'normally closed' approach offers inherent fail-safe operation.
The control panel monitors the circuit's integrity by detecting changes in current flow, with predetermined thresholds for alarm activation.
Advantages
Inherent fail-safe design - cable breaks or power failures trigger alarm.
Simpler circuitry than FSL systems.
Good tamper resistance.
Suitable for most traditional security applications.
Limitations
Cannot pinpoint specific triggered devices.
Limited fault diagnosis capabilities.
Susceptible to bypass attacks if not properly secured.
Higher standby power consumption.

## Slide 11
Fully Supervised Loop (FSL)
Advanced monitoring
FSL circuits utilise end-of-line resistors and precise current/voltage monitoring to detect alarm conditions and circuit faults, including short circuits, open circuits, and earth faults.
Fault discrimination
The system can distinguish between alarm activations and various fault conditions, enabling appropriate response protocols and minimising false alarms.
Configuration flexibility
FSL circuits can be configured to monitor multiple zones, such as fire and security alarms. Used to monitor changes in state in single zones with defined resistance values, offering superior protection for medium to large installations.
Enhanced security
The sophisticated monitoring capabilities significantly increase tamper resistance and system integrity, making FSL circuits suitable for high-security applications.

## Slide 12
Fully Supervised Loop (FSL)
Fully Supervised Loops represent a significant advancement over basic open and closed loop circuits, offering thorough monitoring of both alarm conditions and system integrity.
The precise resistance monitoring enables you to quickly identify and address issues, minimising system downtime.

## Slide 13
End-of-line resistors in FSL
Resistor function
Provides a known termination impedance
allowing the control panel to monitor the
intact circuit.
Typically, 4.7kΩ to 10kΩ depending on system
Must be installed at the furthest point from the panel
Fault detection
Enables the system to distinguish between different circuit states.
Normal: Standard current flow
Alarm: Current change within predefined parameters
Open circuit: No current flow
Short circuit: Excessive current flow
Installation considerations
Correct placement is critical for proper system operation.
Must be precisely valued as specified by manufacturer
Requires secure connections to prevent intermittent faults
Temperature coefficient should match application environment
Troubleshooting
Key diagnostic element in system maintenance.
Voltage measurements across EOL provide diagnostic data
Incorrect values can cause persistent false alarms
Testing should include resistance verification

## Slide 14
End-of-line resistors in FSL
End-of-line resistors are fundamental components in fully supervised loop systems, establishing the circuit's baseline electrical signature.
Their precise values and correct installation are critical to the system's ability to differentiate between normal operation, alarm conditions, and various fault scenarios.

## Slide 15
Addressable circuits: Fire alarms
Digital intelligence
Provides two-way communication with uniquely identified devices
Precise location identification
Pinpoints exact triggered device or fault location
Advanced configuration
Individually programmable device sensitivity and response
Sophisticated alarm logic
Complex cause-and-effect programming for intelligent
response
Remote diagnostics
Comprehensive troubleshooting without physical
access

## Slide 16
Addressable circuits
Addressable circuits represent the highest tier of protection system circuitry, enabling each device on the loop to communicate individually with the control panel.
This technology allows for granular monitoring and control of individual devices, facilitating sophisticated alarm verification and reducing false alarms through intelligent decision-making algorithms.
The digital communication protocol enables not only alarm reporting but also:
detailed diagnostic information
calibration data
contamination levels
allowing for predictive maintenance before failures occur.

## Slide 17
Addressable circuit protocols
Addressable systems use various communication protocols to establish reliable data exchange between the control panel and field devices.
Each protocol offers different capabilities in terms of speed, device capacity, and feature set. When selecting a protocol, consider factors such as system size, response time requirements, and desired functionality.
Most modern addressable systems use sophisticated error detection and correction methods to ensure data integrity even in electrically noisy environments. This resilience makes them particularly well-suited for protecting critical infrastructure.

## Slide 18
Radial circuits
Central distribution
Radial circuits feature a star topology where individual circuits emanate directly from the central control panel. Each circuit serves a specific zone or area, with dedicated wiring running from the panel to the protected space.
Circuit independence
Each radial circuit operates independently, providing isolation between zones. This design ensures that a fault on one circuit doesn't affect the operation of others, improving system resilience and facilitating maintenance and troubleshooting.
Scalability considerations
While radial circuits offer excellent zone isolation, they can require significant wiring for large installations. Designers must balance the benefits of circuit independence against the increased installation costs and potential cable management challenges.

## Slide 19
Radial circuits
Radial circuits are particularly valuable in applications where zone separation is critical, such as in:
hospital wards
industrial facilities with distinct hazard areas
multi-tenant buildings.
Their straightforward topology simplifies fault finding, allowing quick isolation of problems to specific branches without complex diagnostic procedures.
However, the cable requirements can be substantial in large installations, making radial circuits less economical than loop configurations for extensive coverage areas.
Modern hybrid approaches often combine radial principles with addressable technology to leverage the advantages of both.

## Slide 20
Audio/visual circuits
Notification circuit design
Audio/visual circuits distribute power and signals to alarm notification appliances such as sounders, strobes, and voice evacuation speakers. They must deliver sufficient current to operate all connected devices simultaneously during alarm conditions.
Load calculations
Precise load calculations are essential, accounting for the inrush current of signalling devices and ensuring circuit capacity matches the maximum potential demand with appropriate safety margin.
Synchronisation requirements
Modern circuits incorporate sync modules or protocols to ensure all strobes flash in unison across multiple circuits.
Power backup considerations
Audio/visual circuits represent significant power loads during activation. Standby power systems must be sized to support full notification operation for the required duration (typically 30-minutes to 2-hours).

## Slide 21
Audio/visual circuits
Audio/visual circuits are subjected to strict regulatory requirements regarding audibility, visibility, and operational reliability.
Make sure these circuits can function properly under adverse conditions, including partial power failure and during building evacuation scenarios.

## Slide 22
Communication data buses: RS-485
Technical specifications
Differential signalling on twisted pair
Can transfer high speed data up to 10Mbps
Maximum cable length of 1200 metres
Can support multiple units without voltage or data loss.
Noise immunity
RS 485 provides exceptional noise immunity in industrial environments with electrical interference, making it ideal for protection systems in harsh conditions. This is achieved by the cable being wrapped in a shielded metal wrap.
Multipoint capability
The bus supports multiple transmitters and receivers in a multi-drop configuration. Devices can be connected anywhere along the bus rather than just at the ends, providing flexible installation options while maintaining signal integrity through proper termination resistance.

## Slide 23
Communication data buses: RS-485
RS-485 has become the de facto standard for industrial control applications, including:
fire alarm systems
access control
building automation
due to its robust performance characteristics.
The balanced transmission line provides outstanding common-mode noise rejection, allowing reliable communication even in environments with significant electromagnetic interference.
Proper implementation requires attention to termination resistors (typically 120Ω) at both ends of the bus to prevent signal reflections, as well as consideration of ground potential differences between distant nodes in large installations.

## Slide 24
Communication data buses: RS-422
Technical characteristics
RS-422 employs differential signalling similar to RS-485 but is designed for point-to-point or multi-drop configurations with a single driver. It operates at data rates up to 10 Mbps and supports cable lengths up to 1200 metres.
The standard uses separate transmit and receive pairs, allowing full-duplex communication unlike the half-duplex nature of typical RS-485 implementations.
Applications in protection systems
RS-422 is ideal for bidirectional communication between control panels and remote devices, such as in CCTV and access control systems. Its dedicated transmit and receive lines simplify protocols, reducing software complexity and response delays.
Implementation considerations
Requires four wires (two differential pairs)
Supports up to 10 receivers per transmitter
Needs termination resistors matching cable impedance
May require shielding in high-interference environments

## Slide 25
Communication data buses: RS-422
While RS-422 offers advantages in terms of full-duplex operation, its requirement for additional wiring compared to RS-485 means it's typically employed only when the simultaneous bidirectional communication capability justifies the increased installation complexity and cost.

## Slide 26
Communication data buses: RS-232
Legacy interface
Once ubiquitous in computing and control systems
Limited range
Maximum recommended cable length of 15 metres
Modest speed
Practical data rates typically limited to 20 kbps
Noise vulnerability
Single-ended signalling susceptible to interference

## Slide 27
Communication data buses: RS-232
Despite its limitations, RS-232 remains present in protection systems primarily for legacy integration, diagnostic interfaces, and simple point-to-point connections.
Modern systems typically use RS-232 only for local configuration ports or temporary connections during commissioning and maintenance.
The standard uses relatively high voltage levels (±5V to ±15V) compared to modern interfaces, which provides some noise margin but increases power consumption and complicates integration with low-voltage microcontrollers.
Level shifters are commonly required when interfacing RS-232 with contemporary digital circuitry.

## Slide 28
Communication data buses: USB
High speed
USB offers data rates from 1.5 Mbps (Low Speed) to 10 Gbps (USB 3.1), providing ample bandwidth for protection system communications and configuration.
Hot-pluggable
Devices can be connected and disconnected without powering down the system, facilitating on-site maintenance and configuration without service interruption.
Power delivery
USB can supply power to connected devices, eliminating the need for separate power sources for diagnostic tools and configuration interfaces.
Limited range
Standard USB is limited to 5 metres, restricting its use to local connections rather than field device communications in larger systems.

## Slide 29
Communication data buses: USB
In protection systems, USB is primarily employed for configuration interfaces, local diagnostics, and firmware updates rather than for critical communications with field devices. Its commonness makes it convenient for connecting laptops and programming tools to control equipment.
However, USB presents potential security vulnerabilities if left accessible, as it could provide an attack vector for system compromise.
Protection system designs must include appropriate safeguards such as:
physical port protection
authentication requirements
firmware validation
to mitigate these risks.

## Slide 30
Data bus topologies: Linear
Structure
Linear topology, also known as bus topology, consists of a single main cable (backbone) with devices connected directly to this central line. This creates a simple daisy-chain arrangement with termination resistors at both ends to prevent signal reflections.
All devices share the same communication medium, with each having a unique address to distinguish messages intended for specific nodes.
Advantages
Simple installation with minimal cabling.
Easy to extend by adding devices to the main bus.
Well-suited for RS-485 and similar differential protocols.
Lower installation cost compared to star topologies.
Limitations
Cable breaks can disable the entire network.
Signal quality degrades with distance and device count.
Difficult to isolate faults without specialized tools.
Limited redundancy options without additional infrastructure.

## Slide 31
Data bus topologies: Linear
Linear bus topology is commonly employed in smaller to medium-sized protection systems, where simplicity of installation and cost-effectiveness are prioritised.
The structure works particularly well with RS-485 communications, which is designed to support multiple devices on a shared differential pair.

## Slide 32
Data bus topologies: Star
Centralised structure
All devices connect directly to a central hub or switch.
Each device has dedicated connection to central point
No direct device-to-device links
Hub often contains intelligence for routing
Fault isolation
Device or cable failures affect only the
specific branch.
Single point failures don't compromise entire system
Easy identification of problematic connections
Maintenance can occur without full system shutdown

## Slide 33
Data bus topologies: Star
Signal quality
Dedicated paths improve transmission reliability.
Reduced signal degradation and interference.
Consistent performance regardless of system load.
Lower latency for time-critical communications.
Cost considerations
Higher material and installation expenses.
Requires more cabling than linear arrangements.
Central hub represents additional infrastructure.
Installation time typically longer than alternatives.
Star topology is preferred in critical protection systems where reliability and fault tolerance are key concerns.
The centralised system helps to keep track of communication systems and makes it easier to set up backups in case something fails.

## Slide 34
Data bus topologies: Ring
Circular configuration
Devices are connected in a closed loop with each node linked to exactly two others, forming a continuous path for signal transmission.
Path redundancy
Data can travel in either direction, providing automatic alternative routing if a single connection fails, enhancing system resilience.
Token passing
Many ring networks use token-based access control, ensuring orderly communication without collisions and providing deterministic performance.
Fault detection
Ring monitors continuously verify network integrity, with sophisticated systems automatically reconfiguring to isolate faults whilst maintaining operation.

## Slide 35
Data bus topologies: Ring
Ring topologies are increasingly employed in advanced protection systems where continuous operation must be maintained even during partial communication failures. Modern implementations often incorporate dual counter-rotating rings for enhanced redundancy, ensuring that two simultaneous failures would be required to isolate any device.
While more complex to implement than linear or star arrangements, ring topologies offer exceptional resilience for critical infrastructure protection, particularly in applications such as industrial safety systems, power distribution protection, and life safety networks.

## Slide 36
Data bus topologies: Mesh
Multiple interconnections
Devices connect to multiple peers creating redundant paths
Dynamic routing
Messages automatically find optimal available path
Superior fault tolerance
Network continues despite multiple simultaneous failures
Self-healing capability
System automatically reconfigures around damaged sections
3

## Slide 37
Data bus topologies: Mesh
Mesh topologies represent the pinnacle of resilience in protection system networking, offering exceptional fault tolerance through redundant interconnections. Each device in a mesh network can communicate with multiple others, creating numerous potential paths for data transmission that automatically adapt to changing conditions.
While full mesh networks (where every device connects directly to every other) become impractical for larger systems due to the exponential growth in connection count, partial mesh topologies strategically implement redundant links at critical points. This balanced approach delivers high reliability while managing complexity and installation costs, making it suitable for high-security applications and critical infrastructure protection.

## Slide 38
Wireless protection circuits
Radio technologies
Proprietary protocols for enhanced security.
Mesh networking for improved coverage and reliability.
Key advantages
Rapid deployment without extensive wiring.
Installation in heritage buildings with minimal disruption.
Flexibility for temporary or relocatable protection.
Reduced installation labour and associated costs.
Critical limitations
Battery dependency creates maintenance requirements.
Potential interference from other radio systems.
Signal attenuation through building structures.
Cybersecurity concerns requiring encryption and authentication.

## Slide 39
Wireless protection circuits
Wireless protection circuits have evolved significantly in recent years, with modern systems offering reliability levels approaching those of wired solutions.
Sophisticated frequency-hopping, spread-spectrum techniques, and intelligent power management have addressed many traditional concerns about wireless reliability.
Contemporary designs typically employ bidirectional communication protocols that enable devices to acknowledge commands and report their status, allowing for comprehensive system monitoring.
This contrasts with earlier one-way systems that could not verify message delivery or device condition.

## Slide 40
Wireless system supervision
Supervision of wireless protection circuits requires careful consideration of the trade-off between timely fault detection and battery conservation. Each wireless device periodically transmits status messages (known as "check-ins" or "heartbeats") to confirm its operational status to the control panel.
Modern systems employ adaptive supervision strategies where check-in intervals dynamically adjust based on environmental conditions, system state, and risk level. During high-risk periods or alarm situations, devices may increase their reporting frequency to provide near real-time status updates at the expense of accelerated battery consumption.
Sophisticated wireless protocols also include signal strength reporting (RSSI), allowing the system to identify marginal communication links before they fail completely, enabling proactive maintenance.

## Slide 41
AC power supplies
Primary power source
AC mains typically provide the principal power for protection systems through dedicated circuits. Regulations often require these circuits to be separately protected and installed by a qualified electrician.
Power conditioning
This is incorporated to shield sensitive electronics from mains disturbances. It includes surge protection, filtering for electromagnetic interference, and in critical applications, isolation transformers to prevent ground loops.
Voltage regulation
Voltage regulation circuits maintain stable output despite fluctuations in mains voltage. Modern switch-mode power supplies provide high efficiency and excellent regulation across wide input voltage ranges.
Monitoring requirements
AC power supplies must include comprehensive monitoring of input voltage, output parameters, and fault conditions. Any power anomalies must generate appropriate fault signals to alert potential issues.

## Slide 42
AC power supplies
AC power supplies used in protection systems must meet strict standards for reliability, electromagnetic compatibility, and thermal performance. Modern designs prioritise high efficiency to reduce heat and operating costs, while ensuring dependable operation under challenging conditions.
In fire and security systems, AC power is converted from unregulated alternating current into regulated and smoothed direct current (DC), which powers most control equipment. This conversion ensures stable and safe operation of critical components.

## Slide 43
DC power supplies
Conversion technology
Modern DC power supplies primarily employ switch-mode technology for high efficiency (typically 85-93%) and reduced heat generation. These supplies convert AC input to regulated DC output through high-frequency switching techniques.
Critical components include power factor correction circuits, switching controllers, isolation transformers, rectification stages, and output filtering to ensure clean DC power.
Battery integration
DC supplies incorporate sophisticated battery charging and monitoring systems. The charging circuit must provide temperature-compensated charging profiles to maximise battery lifespan while ensuring full capacity is maintained.
Advanced systems include impedance monitoring to detect battery deterioration before capacity is significantly reduced, allowing proactive replacement before system reliability is compromised.

## Slide 44
DC power supplies
Distribution design
DC distribution systems feature overcurrent protection for each circuit, usually through resettable PTC devices or electronic current limiting rather than fuses that require physical replacement.
Voltage supervision on individual outputs detects load-specific issues, while ground fault monitoring identifies insulation breaches that could compromise system integrity or create safety hazards.
DC power supplies must maintain strict output voltage tolerance (typically ±5%) under all load conditions to ensure reliable operation of electronic components.
For critical protection systems, redundant power supply modules with automatic load sharing ensure continuous operation even in the event of component failures.

## Slide 45
Battery backup systems
Modern protection systems employ deep-cycle sealed lead-acid or lithium iron phosphate (LiFePO4) batteries specifically designed for standby applications. These batteries must deliver reliable power during extended outages while maintaining sufficient capacity to drive high-current loads like sounders and strobes during alarm conditions.
Comprehensive battery management includes temperature-compensated charging, regular capacity testing, and detailed condition monitoring. Advanced systems perform automatic load tests by briefly transferring to battery power to verify real-world performance under actual load conditions.
Battery backup systems provide secondary power during mains failures, ensuring continuous protection system operation. Design requirements vary by application and relevant standards, with fire protection typically requiring longer autonomy than security systems.

## Slide 46
Effects of series resistance
Voltage division
Series resistance creates voltage drops proportional to current flow according to Ohm's Law (V=IR). This reduces the voltage available to downstream devices, potentially compromising their operation.
Current limitation
Total circuit current becomes limited by the ratio of supply voltage to total circuit resistance. As series resistance increases, maximum available current decreases, potentially preventing devices from activating.
Power dissipation
Series resistance dissipates power according to P=I²R, converting electrical energy to heat. This represents energy unavailable to functional devices and creates thermal management challenges.
Signal distortion
In data circuits, series resistance combined with circuit capacitance creates low-pass filter effects, potentially distorting digital signals and causing communication errors at higher frequencies.

## Slide 47
Effects of series resistance
Series resistance in protection circuits comes from multiple sources including:
cable resistance
connection impedance
component internal resistance
intentionally added current-limiting resistors.
While some series resistance is inevitable, excessive values compromise system performance and reliability.
Engineers must calculate total series resistance during design to ensure adequate voltage at the furthest devices even under worst-case conditions such as:
minimum supply voltage
maximum load, and
end-of-life battery capacity.

## Slide 48
Effects of parallel resistance
Current distribution
Current divides between parallel paths inversely proportional to their resistance values, following I₁/I₂ = R₂/R₁
Total resistance reduction
Parallel paths reduce overall circuit resistance according to 1/Rₜ = 1/R₁ + 1/R₂ + ... + 1/Rₙ
Increased load current
Lower effective resistance draws higher current from power supplies, potentially exceeding their capacity
3
Fault path creation
Unintended parallel paths can bypass protective elements and create security vulnerabilities

## Slide 49
Effects of parallel resistance
Parallel resistance configurations in protection systems can be both intentional design elements and unintended consequences of installation errors.
Properly designed parallel circuits distribute load across multiple paths, reducing voltage drop and increasing system capacity. However, unintended parallel paths can compromise supervised circuits by creating alternative routes that bypass detection devices.
In addressable systems, parallel branches must be carefully controlled to maintain signal integrity. Excessive branching can create impedance mismatches and signal reflections that degrade digital communication reliability, particularly at higher data rates.
Star configurations from central hubs are preferred over unstructured parallel branching for this reason.

## Slide 50
End-of-line device configurations
Basic EOL monitoring
Simple end-of-line resistor configurations use a single resistor to establish a baseline current. The control panel distinguishes between normal state, alarm activation (parallel resistance), and line fault conditions (open or short circuit).
Dual EOL configuration
Dual resistor arrangements provide more sophisticated monitoring by establishing distinct resistance values for normal, alarm, and tamper conditions. This allows the system to differentiate between actual alarms and attempted circuit tampering.
Active EOL modules
Advanced systems employ active end-of-line modules with microprocessors that continuously monitor line conditions and communicate detailed diagnostic information. These devices can detect subtle changes in circuit parameters before they develop into actual faults.

## Slide 51
End-of-line device configurations
End-of-line configurations must be meticulously matched to control panel specifications to ensure proper operation.
Resistance values typically range from 1kΩ to 10kΩ depending on the manufacturer and are selected to optimise the balance between current consumption and noise immunity.

## Slide 52
Voltage drop calculation
V = IR
Basic formula
Ohm's Law defines the fundamental relationship between voltage drop, current flow, and circuit resistance.
ΔV = 2 × I × L × mV
Practical calculation
In this formula, ΔV is the voltage drop in volts, I is the current in amperes, L is the length of the cable run in metres, and mV is the voltage drop per ampere per metre taken from cable tables (expressed in millivolts). The division by 1000 converts millivolts to volts, making the result easier to interpret.
5-10%
Maximum
allowable drop
Industry standards typically limit voltage drop to ensure reliable operation of all devices.

## Slide 53
Voltage drop calculation
Voltage drop calculations are essential for protection system design, particularly for circuits extending over long distances or supplying high-current loads such as sounders and strobes. Excessive voltage drop can prevent devices from operating correctly, especially during alarm conditions when current demand peaks.
Engineers must calculate the worst-case scenario, which typically occurs at minimum supply voltage (often end-of-life battery voltage) with maximum current draw (full alarm load) and highest expected ambient temperature (which increases conductor resistance). The cumulative voltage drop across all series elements including cables, connection points, and current-limiting components must remain within the device's operating tolerance.
For critical circuits, spot voltage measurements should be taken at commissioning to verify calculations and ensure adequate voltage at the furthest devices.

## Slide 54
Effects of voltage drop on devices
Sounders
Reduced sound pressure level with decreasing voltage. A 10% voltage drop typically results in a 3-4 dB reduction in output, potentially falling below regulatory minimum levels.
Visual indicators
Decreased light output and flash energy, reducing visibility and potentially failing to meet standards for strobe intensity in emergency notification applications.
Electronic devices
Unpredictable behavior when operating below design specifications, including failure to respond to commands, intermittent operation, or complete non-function.
Wireless transmitters
Reduced transmission range and reliability due to lower RF output power, potentially creating communication dead zones not present during normal voltage conditions.

## Slide 55
Effects of voltage drop on devices
Protection system devices are designed to operate within specific voltage ranges, typically with a lower limit of 18-21V for nominal 24V systems. When supply voltage falls below these thresholds due to excessive voltage drop, device performance degrades progressively.
This degradation is particularly problematic during alarm conditions when system load is highest, and battery voltage may already be reduced from extended operation.
Engineers must dimension power supplies, batteries, and conductors to maintain adequate voltage even under these adverse conditions, ensuring reliable operation when the system is most needed.

## Slide 56
Protection systems in electrically noisy environments
Identify interference sources
Map potential EMI sources including motors, inverters, radio transmitters
2
Implement shielding
Use properly grounded cable shields and metallic enclosures
Separate cable routes
Maintain distance between signal and power conductors
Apply filtering techniques
Incorporate ferrites, filters, and isolation barriers

## Slide 57
Protection systems in electrically noisy environments
Protection systems must operate reliably even in environments with significant electromagnetic interference (EMI). Industrial facilities, data centres, and areas with high-power equipment present particularly challenging conditions that can disrupt normal circuit operation through induced voltages and currents.
For digital communication lines, differential signalling technologies such as RS-485 provide significant common-mode noise rejection. These should be implemented with twisted pair cabling to minimize electromagnetic pickup. For particularly severe environments, fibre optic connections offer complete electrical isolation and immunity to electromagnetic interference, albeit at higher installation cost.
Power supplies should incorporate extensive filtering to prevent noise ingress through the mains connection, while signal lines may require additional surge suppression to handle transient events.

## Slide 58
Lightning and surge protection
Why it matters Lightning strikes and electrical surges can damage equipment, disrupt systems, and pose safety risks.
Protection systems help reduce these risks.
Key concepts
Lightning Protection Systems (LPS):
Use air terminals, conductors, and earth rods to safely direct lightning to ground.
Surge Protection Devices (SPDs):
Installed in electrical panels to absorb and divert excess voltage from surges caused by lightning or switching events.

## Slide 59
Lightning and surge protection
Lightning and surge protection for protection systems must be approached as a coordinated system rather than a collection of individual devices.
The protection strategy should address all potential entry paths including:
power
signal
data lines
with particular attention to interfaces between buildings or between indoor and outdoor environments.

## Slide 60
Grounding and noise reduction techniques
Basic signal protection concepts
Grounding To avoid electrical interference, all components of a protection system should be connected to a single grounding point - typically located at the main control panel. This helps prevent unwanted current loops that can cause faults or false signals.
Twisted pair cables Using twisted pair cables helps reduce noise. As the wires are twisted together, they pick up interference equally, which cancels it out and keeps the signal clean.
Filtering Filters are used to block unwanted electrical noise from entering the system. These are placed where power or signal cables connect to equipment, helping keep the system stable and reliable.

## Slide 61
Grounding and noise reduction techniques
Effective grounding and noise reduction strategies are essential for ensuring protection system reliability, particularly in challenging environments with multiple electronic systems and potential interference sources.
These techniques must be implemented during initial installation, as retrofitting proper grounding can be difficult and costly.

## Slide 62
Circuit segregation and isolation
Functional segregation
Protection systems should maintain clear separation between circuit types based on function and electrical characteristics. Power distribution, control signals, and communication circuits should occupy distinct physical spaces within enclosures and follow separate cable routes throughout the installation.
Voltage level isolation
Circuits operating at different voltage levels must be physically separated according to relevant electrical codes. High-voltage and low-voltage circuits require specific minimum separation distances or physical barriers. This separation prevents insulation breakdown and reduces capacitive coupling between circuits.
Galvanic isolation
Critical interfaces between different system sections should employ galvanic isolation techniques to prevent fault propagation. Optical isolators, isolation transformers, and relay interfaces create distinct electrical domains that contain faults within their respective sections, preventing cascading failures across the entire system.

## Slide 63
Circuit segregation and isolation
Proper circuit segregation is a fundamental principle in protection system design that enhances both safety and reliability.
By maintaining appropriate separation between different circuit types, the system becomes more resilient against cross-interference, easier to maintain, and less susceptible to common-mode failures affecting multiple subsystems simultaneously.
Modern protection systems often employ modular architectures where different functions are implemented on separate circuit boards or in distinct enclosures.
This approach facilitates both physical segregation and selective isolation, allowing for graceful degradation rather than complete system failure when problems occur.

## Slide 64
System reliability and redundancy
Fire Alarm Systems (BS 5839-1)
Wiring: Fault-tolerant/bi-directional loops (often called Class A in NFPA).
Power: Mains supply + 24-hour standby batteries.
Control: Distributed loop cards to limit single points of failure.
Comms: Redundant links between networked panels.
Example: Hospitals use fault-tolerant loops, so devices still operate after a single open/short circuit fault.

## Slide 65
System reliability and redundancy
Intruder Alarm Systems (BS EN 50131 / PD 6662)
Wiring: Supervised loops with end-of-line (EOL) monitoring.
Power: Standby batteries sized for required Grade (12–60 hrs).
Control: Grade 3/4 systems use tamper monitoring on all devices.
Comms: Dual-path signalling (IP + GPRS/4G) to ARC.
Example: High-risk jewellery store → dual-path signalling ensures alarm still transmits if broadband fails.

## Slide 66
System reliability and redundancy
Access Control Systems (BS EN 60839)
Wiring: Local door controllers isolate faults.
Power: Each controller fitted with standby battery/UPS.
Control: Redundant server/database or distributed architecture.
Comms: Controllers continue operating in offline/fallback mode.
Example: Data centres → local door units keep secure doors locked/unlocked to rules even if comms server fails.

## Slide 67
System reliability and redundancy
CCTV Systems (BS EN 62676)
Wiring: Resilient PoE switches and ring-based network topologies.
Power: UPS to protect cameras, NVRs, and network.
Control: RAID storage arrays or mirrored NVRs.
Comms: Dual recording paths (edge + central storage).
Example: Casinos → RAID + dual NVR ensures no footage loss during drive or network failure.

## Slide 68: Summary
You should now be able to:
Understand protection system circuit configurations.
Interpret protection system wiring schematics.
Check and verify basic circuit continuity and functionality.

## Slide 69
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.