## Slide 1
Occupational Specialism: Protection Systems Engineering
K1.12 Inspections of protection systems
PowerPoint 12: Inspections of protection systems

## Slide 2: Introduction
This session covers the standard procedures and processes for making visual, physical, and electrical inspections in accordance with current industry standards and codes of practice.
It provides detailed methodologies, essential checklists, and practical advice to ensure your inspection processes are comprehensive and compliant.

## Slide 3: Objectives
By the end of this session, you should be able to:
Understand common faults found in protection systems
Use test equipment and fault-finding techniques
Record, report, and resolve system faults

## Slide 4
Overview
Introduction to inspection requirements
Overview of regulatory framework and compliance objectives
Visual inspection procedures
Comprehensive assessment of visible system components
Physical verification methods
Hands-on testing of mechanical integrity and installation quality
Documentation and O&M manual integration
Record-keeping requirements and system documentation

## Slide 5
Regulatory framework and standards compliance
British Standards
BS EN 50131 (intrusion systems), BS 5839 (fire detection), BS EN 50132 (CCTV), and BS EN 50133 (access control) provide detailed frameworks for system inspection and commissioning.
Regulatory requirements
The Regulatory Reform (Fire Safety) Order 2005, Electricity at Work Regulations 1989, and Building Regulations provide legal basis for inspection standards in the UK.
Industry best practices
BSIA (British Security Industry Association) guidelines, NSI (National Security Inspectorate) Gold standards, and SSAIB (Security Systems and Alarms Inspection Board) criteria establish quality benchmarks.

## Slide 6
Pre-inspection planning and preparation
Documentation review
Gather and examine all relevant system documentation, including design specifications, manufacturer's manuals, and previous inspection reports. Cross-reference these documents with current installation to identify potential discrepancies.
Equipment calibration
Ensure all testing equipment is properly calibrated and certified for accurate measurements. This includes multimeters, earth resistance testers, and specialist tools required for specific system types.
Risk assessment
Conduct a thorough risk assessment of the inspection environment, identifying potential hazards such as live electrical components, working at height, or confined spaces. Develop appropriate control measures to mitigate risks.

## Slide 7
Personal protective equipment requirements
Eye protection
Safety glasses or goggles when drilling, fixing, or working in dusty areas.
Gloves
Lightweight cut-resistant or general site gloves for handling fixings, trunking, and sharp cable ends.
Footwear
Safety boots with slip resistance and toe protection.
Working at height
Use step ladders or podiums safely,
with three points of contact.
Additional site PPE
Hi-vis vest
Hearing protection
Dust mask if required by site rules.

## Slide 8
Required testing equipment and tools
Electrical measurement devices
Calibrated digital multimeter
Insulation resistance tester (1kV minimum)
Earth loop impedance tester
Non-contact voltage detector
System-specific test equipment
Fire alarm test kit with smoke/heat simulators
CCTV test monitor with signal analysers
Cable tracer and identifier
Hand tools and accessories
Insulated screwdriver set (VDE certified)
Terminal torque screwdrivers
Cable preparation tools

## Slide 9
Visual inspection: system documentation
Required documentation
Every protection system must maintain a comprehensive documentation package that serves as the authoritative reference for the installation. This includes detailed system schematics, zone plans, component specifications, and commissioning certificates.
Verify that all documentation is current, properly filed, and readily accessible to authorised personnel.
Documentation should be protected from damage and deterioration, with digital backup copies maintained where appropriate.
Documentation review procedure
Confirm documentation matches installed system configuration
Verify all modifications are properly documented with change control records
Check that system certificates are valid and current
Ensure operation and maintenance manuals are available
Confirm logbooks are properly maintained with accurate service history

## Slide 10
Visual inspection: control panels and interfaces
Physical condition Check the housing for damage, loose fittings, missing screws, or signs of tampering.
Labelling and identification Confirm that panels, circuits, and interfaces are clearly labelled and match site drawings.
Cabling and terminations Ensure cables are neatly dressed, secure, and free from signs of overheating or damage.
Indicators and displays Verify that LEDs, screens, and labels are working, visible, and not obscured.

## Slide 11
Visual inspection: field devices and sensors
CCTV cameras
Inspect for proper mounting, alignment, and field of view.
Check for physical damage, lens obstruction, and cable integrity.
Verify weatherproof housings are intact with no moisture ingress.
Fire detectors
Verify correct positioning according to BS 5839.
Check for dust accumulation, tampering, or physical damage. Confirm indicator LEDs function properly and that detector type is appropriate for the protected area.
Access control devices
Inspect readers, keypads, and biometric devices for physical damage and tampering.
Verify proper mounting height and orientation. Check that status indicators function correctly.
Intruder detection sensors
Check PIR sensors, door contacts, and glass break detectors for mounting security and alignment. Verify detection coverage patterns and ensure sensors are free from obstructions.

## Slide 12
Visual inspection: cabling infrastructure
Cable routing inspection
Verify that cables follow designated routes with proper support. Check that cables maintain minimum separation distances from potential interference sources. Ensure cables are not damaged, pinched, or excessively bent.
Cable identification assessment
Confirm all cables are clearly labeled at both ends and at intermediate points for long runs. Verify labels match system documentation and are made from durable materials resistant to environmental degradation. Check that colour coding or numerical systems are consistently applied.
Cable protection verification
Inspect cable containment systems (conduits, trunking, trays) for physical integrity and appropriate fill ratio. Check that cables in vulnerable areas have additional mechanical protection.
Termination examination
Inspect terminations for neatness, proper technique, and appropriate strain relief. Check that junction boxes are accessible, properly covered, and contain no unauthorised connections.

## Slide 13
Visual inspection: power supplies and backup systems
Primary power input
Verify correct input voltage and that electrical connections are secure. Check that supply is from a dedicated circuit with appropriate overcurrent protection. Confirm proper grounding and that electrical isolation means are clearly identified.
Backup batteries
Inspect batteries for physical damage, leakage, or bulging. Verify installation date is marked and batteries are within service life. Check for appropriate ventilation when required. Confirm battery terminals are clean, tight, and protected against accidental shorting.
Power distribution
Examine output terminals for secure connections and correct polarity markings. Verify fuses or circuit breakers are of correct rating and properly labeled. Check that load distribution is balanced and within rated capacity of the power supply.
Thermal conditions
Check for adequate ventilation around power supplies and that cooling vents are unobstructed. Verify that power components are not operating at excessive temperatures. Confirm thermal protection mechanisms are functioning correctly.

## Slide 14
Visual inspection: environmental conditions
Temperature and humidity
Verify that ambient conditions are within manufacturer's specified operating ranges. Typical electronic protection equipment requires 5-35°C and 10-90% non-condensing humidity. Check that temperature and humidity monitoring systems, where fitted, are functioning correctly.
Inspect for signs of condensation, water ingress, or excessive heat that could affect system reliability. Confirm that HVAC systems serving equipment rooms are operating properly with appropriate maintenance records.
Dust and contaminants
Assess cleanliness of equipment areas and inspect for dust accumulation on electronic components and ventilation openings. Verify that cabinet filters, where fitted, are clean and properly installed.
Check that equipment in harsh environments has appropriate IP-rated enclosures intact and that gaskets and seals are in good condition. Confirm that chemical or corrosive atmospheres are mitigated with appropriate protective measures.
Water and moisture risks
Inspect for potential water hazards such as overhead pipes, condensation drips, or flood risks. Verify that equipment is mounted at appropriate heights in areas with flood potential.
Check that outdoor equipment has proper drainage, correctly fitted weatherproof covers, and appropriate heaters/thermostats to prevent condensation where required.

## Slide 15
Physical checks: water ingress protection
Visual inspection of seals and gaskets
Check for deterioration, cracking or compression set
Verification of cable entry points
Examine glands, grommets and penetration seals
Assessment of drainage provisions
Confirm condensation drain holes are clear

## Slide 16
Physical checks: tamper protection
Enclosure tamper switches
Verify that tamper switches are correctly positioned to detect unauthorised access to equipment enclosures.
Test the operation of each switch by carefully opening covers and doors, confirming that the system registers and reports tamper events as configured.
Check that tamper switches are securely mounted with proper alignment that prevents false alarms from vibration or thermal expansion.
Confirm that tamper circuits remain active even when the system is in maintenance mode, as required by BS EN 50131-1 for Grade 3 and 4 systems.

## Slide 17
Physical checks: tamper protection
Tamper-evident seals
Inspect all tamper-evident seals for signs of tampering or attempted removal.
Verify that seal serial numbers match those recorded in system documentation and that seals are properly applied to prevent access without destruction of the seal.
Confirm that appropriate seal types are used based on security requirements - from simple adhesive seals for lower security applications to sophisticated holographic or wire seals for high-security installations.
Replace any damaged or missing seals according to established procedures.

## Slide 18
Physical checks: labelling and identification
Proper labelling is essential for efficient system maintenance and troubleshooting. Verify that all components have durable identification that corresponds to system documentation. Labels should be easy to locate.
Confirm that emergency procedures and contact information are clearly displayed at main control points in accordance with BS 5839-1 and BS EN 50131-1 requirements.

## Slide 19
Documentation and O&M manual requirements
Essential documentation components
System design specifications and performance criteria
As-built drawings showing actual installation details
Block and schematic diagrams of system architecture
Component data sheets and manufacturer documentation
Software versions and firmware revisions
Commissioning test results and certification
Maintenance schedules and procedures
Operating instructions
Normal operating procedures for end users
Routine testing instructions for system administrators
Fault finding and troubleshooting guides
Emergency procedures and fallback operations
User-level maintenance activities and schedules
System limitations and known issues
Contact information for technical support
Regulatory compliance records
Completion certificates to relevant standards
Regulatory compliance declarations
Inspection and test schedules
Historical record of system modifications
Calibration certificates for test equipment
Training records for system operators
Risk assessments and method statements

## Slide 20: Summary
You should now be able to:
Understand common faults found in protection systems
Use test equipment and fault-finding techniques
Record, report, and resolve system faults

## Slide 21
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.