## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.7 Design concepts of installations specified in national standards
PowerPoint 1.7: Design concepts

## Slide 2: Introduction
What processes would be essential when considering the design of a13 A power socket for residential use?

## Slide 3: Objectives
By the end of this session, you should be able to:
Understand requirements relating to electrical design
Understand processes involved in electrical design

## Slide 4: Importance of BS 7671 in electrical design
BS 7671 known as the IET Wiring Regulations, is the fundamental standard for electrical installation design in the UK.
It sets out the minimum safety and performance requirements for systems in domestic, commercial, and industrial environments.
All electrical design decisions must be aligned with BS 7671 to ensure legal compliance, particularly under the Electricity at Work Regulations 1989, which require installations to be constructed and maintained to prevent danger.

## Slide 5: The role of BS 7671 in the design process
Designing an electrical installation using BS 7671 goes beyond simply selecting cable sizes and protective devices. The designer must consider environmental conditions, installation methods, accessibility, future maintenance, and safety requirements.
The regulations provide a framework that guides every design decision, from circuit layout to the selection of protective measures. This ensures that installations are not only safe at the time of installation but remain safe throughout their operational life.

## Slide 6: Why BS 7671 must be referenced from the start
BS 7671 should be consulted during the earliest stages of system planning. Referencing the regulations from the outset ensures that layout, containment systems, cable routing, and protection devices are all compliant and suitable for the specific installation.
This proactive approach leads to safer, more efficient, and maintainable electrical systems and helps avoid costly rework or non-compliance issues later in the project.

## Slide 7: Purpose of Part 4 in BS 7671
Part 4 of BS 7671 outlines the measures that must be implemented in an installation to ensure protection for safety. This section defines how systems are designed to safeguard persons, property, and livestock from the dangers of electricity under both normal and fault conditions.
It serves as the foundation for selecting appropriate protection methods that meet both legal and functional requirements.
These include electric shock protection, overcurrent protection, and voltage disturbance mitigation.

## Slide 8: Electric shock protection – Chapter 41
Chapter 41 covers protection against electric shock. One of the most important methods is automatic disconnection of supply (ADS), which ensures a fault is cleared quickly before danger arises.
Designers must ensure that the selected protective device, such as an MCB or RCD, will disconnect the supply within the maximum permitted disconnection time.
Factors like earthing type (TT, TN-S, etc.), circuit impedance, and circuit use influence the need for RCD protection, particularly for socket outlets, outdoor circuits, or bathroom installations.

## Slide 9: Overcurrent protection: Chapter 43
Overcurrent protection is addressed in Chapter 43 and includes protection against both overload currents and short-circuit faults.
A key part of design is selecting a protective device (e.g. fuse, MCB, RCBO) that matches the expected load without nuisance tripping, yet will operate within safe time limits under fault conditions.
Designers must verify that cables are protected in accordance with their current-carrying capacity and ensure the protective device has a breaking capacity that matches the potential fault current available at its location.

## Slide 10: Overvoltage and surge protection: Chapter 44
Chapter 44 addresses protection against voltage disturbances such as transient over-voltages, switching surges, and electromagnetic interference.
The designer must assess the need for Surge Protective Devices (SPDs), especially where sensitive electronic equipment is present, or where over-voltages could affect safety (e.g. medical facilities or fire alarm systems).
Notes: https://electrical.theiet.org/wiring-matters/years/2023/98-november-2023/surge-protective-devices-spds/

## Slide 11: Part 5: Equipment selection and installation
Part 5 of BS 7671 sets the standard for selecting and erecting electrical equipment.
During the design stage, the installer must ensure all components -such as wiring systems, control gear and accessories - are suitable for the installation conditions.
These include not only the operational requirements of the load but also the physical and environmental characteristics of the site.
Selection must account for safety, durability, accessibility, and compliance with all relevant regulations within BS 7671.

## Slide 12: External influences and Regulation Group 522
One of the key design considerations covered in Part 5 is how equipment performs under external influences, detailed in Regulation Group 522.
Designers must assess the installation environment and apply relevant codes (from Appendix 5) that identify risks such as corrosion (AF), temperature extremes (AE), humidity (AG), or mechanical stress (AD).
For example, in an agricultural building, cables may be subject to high levels of moisture and impact, so materials with suitable ingress protection and mechanical strength must be selected. Failing to do so can compromise safety and lead to early system failure.

## Slide 13: Manufacturer data and installation requirements
In addition to BS 7671 requirements, designers must also follow manufacturer instructions as per Regulation 134.1.1.
This means technical data sheets and product literature must be reviewed during the design phase to ensure compatibility and correct installation.
For example, circuit breakers and RCDs often have specific installation orientations, derating considerations, or mounting limitations.
The designer’s role is to verify that all selected equipment is installed within the limits defined by both the Regs and the manufacturer to ensure safety, performance, and warranty validity.

## Slide 14: Using Appendix 4 for current-carrying capacity
Appendix 4 of BS 7671 provides calculations, tables and correction factors needed to determine the current-carrying capacity (Iz) of cables under real-world conditions.
During design, the electrician must verify that each cable is capable of carrying the required current without exceeding its temperature rating. This involves using tables for conductor type, insulation material, installation method, and ambient temperature.
The tables allow designers to determine a base value, which is then modified by relevant correction factors to give an adjusted capacity. This ensures the cable will operate safely over time without overheating or degrading.

## Slide 15: Voltage drop and energy performance
Designers must calculate the voltage drop in each circuit, especially for long cable runs or high-load installations. Appendix 4 provides tabulated mV/A/m values based on cable type and installation method. These values are used to verify that the total voltage drop does not exceed the maximum allowable limits:
3% for lighting circuits
5% for other circuits (e.g. sockets, appliances).
Excessive voltage drop can reduce the efficiency of connected equipment, cause flickering lights, or increase energy losses. Good design ensures voltage levels are stable under normal operating conditions, preserving safety and functionality.

## Slide 16: Understanding protection coordination
Protection coordination refers to the process of ensuring that all protective devices within an installation are selected and arranged so that, during a fault, only the device closest to the fault operates.
This avoids unnecessary loss of supply to healthy parts of the installation.
Coordination is a crucial consideration in multi-board installations, distribution systems, and commercial or industrial sites where continuity of supply is essential.
BS 7671 does not mandate coordination directly but supports it through correct application of breaking capacities, disconnection times, and circuit layouts.

## Slide 17: Selectivity between protective devices
Selectivity (also known as discrimination) is a design approach that ensures fault conditions are cleared by the correct device without affecting other circuits.
This is especially important in systems using cascaded devices like fuses and MCBs or upstream RCDs and RCBOs. Designers must consider time-current characteristics when selecting devices.
BS 7671 offers guidance through coordination charts and time/current curves in Appendix 3 and manufacturer data must also be consulted.

## Slide 18: Common issues and good practice
Poor selectivity can lead to nuisance tripping, where a fault on one circuit causes the upstream main switch or RCD to trip, cutting power to unaffected areas.
To avoid this, designers should avoid over-reliance on a single RCD protecting multiple circuits and instead specify RCBOs where selectivity is critical.
Similarly, using a mix of protective devices with incompatible time characteristics can compromise system integrity.
Good practice includes limiting the number of final circuits per RCD, avoiding excessive circuit stacking on distribution boards, and using manufacturer discrimination data to inform device pairing.

## Slide 19: Principles of circuit layout design
When designing an installation, circuit layout must be planned to ensure safe, logical, and maintainable distribution of electrical power.
This involves deciding how many circuits are needed, how they are divided across distribution boards, and which loads are grouped together.
A good layout balances the load across phases where applicable, minimises cable lengths, and considers future expansion. It also supports ease of isolation and fault diagnosis.
The layout is typically represented through circuit schedules, wiring diagrams, and distribution board labels that reflect the final installation.

## Slide 20: Functional and safety-based circuit separation
Circuit separation is not just about convenience; it’s a regulatory requirement in some situations.
BS 7671 requires certain circuits to be separated for safety or functional reasons.
For example, lighting and socket outlets should be on separate circuits so that a fault on one does not leave occupants in darkness.
Life-safety systems such as smoke alarms must be on independent, clearly labelled circuits. Similarly, kitchens and bathrooms may require separation due to environmental risks and power demands. The design must consider both user safety and system resilience.

## Slide 21: Design strategies for circuit grouping
Group circuits logically according to function and usage area.
For example, all kitchen socket outlets could be on a single circuit, while another is dedicated to heating controls or outdoor power.
Grouping helps with load calculation, fault finding, and future upgrades.
Designers must also consider selectivity requirements, avoiding excessive reliance on one RCD, and avoid placing high-load or frequently used appliances on shared circuits with sensitive equipment.
Where possible, leave space in distribution boards for future additions, ensuring that the physical layout reflects the design logic.

## Slide 22: Summary
You should now be able to:
Understand requirements relating to electrical design
Understand processes involved in electrical design

## Slide 23
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.