## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.5e Application of the fundamental principles of national standards
PowerPoint 1.5e: Chapter 56

## Slide 2: Introduction
If the mains fails during a fire, name which electrical systems that must keep working, and why?

## Slide 3: Objectives
By the end of this session, you should be able to:
Define a safety service and give common examples
Differentiate automatic vs non-automatic sources

## Slide 4: 560.1: Scope
This chapter covers general requirements for safety services, selection and erection of electrical supply systems for safety services and electrical safety sources. Standby electrical supply systems are outside the scope of this chapter.
This chapter does not apply to installations in hazardous areas (BE3), for which requirements are given in BS EN 60079-14.

## Slide 5: 560.1
Examples of safety services (this list is not exhaustive):
Emergency lighting
Fire detection and alarm systems
CO detection and alarm systems
Fire evacuation systems
Smoke ventilation systems
Fire services communication systems
Essential medical systems.

## Slide 6: Safety services
From Part 2: A safety service is defined as: ‘an electrical system for electrical equipment provided to protect or warn persons in the event of a hazard, or essential to their evacuation from a location’.
Such services are commonly employed in buildings open to the public and general commercial and industrial premises.

## Slide 7: 560.4: Classification
An electrical safety service supply is classified as either:
a non-automatic supply
an automatic supply.
See BS 7671 560.4.1 for a description of types of safety services.
560.5.1: Safety services may be required to operate at all relevant times including during mains and local supply failure and through fire conditions.

## Slide 8: 560.6.1: Electrical sources for safety services
The following electrical sources for safety services are recognised:
storage batteries
primary cells
generator sets independent of the normal supply
a separate feeder of the supply network that is effectively independent of the normal feeder.

## Slide 9: 560.6.10 and 560.6.11
Batteries used as the supply for safety services are classified into two categories:
central-power supply sources
low-power supply sources, the low-power source being limited to 1,500 watt-hours.

## Slide 10: 560.6.12: Uninterruptible power supply sources (UPS)
These types of devices maintain a continuous supply to connected equipment by supplying power following the failure of the primary source.
They can be either static (delivering an output voltage from a stored source through a converter) or rotary (for example, a diesel-driven generator).

## Slide 11: 560.6.14: Monitoring of safety services
The condition of the source for safety services (ready for operation, under fault conditions, feeding from the source for safety services) shall be monitored.

## Slide 12: 560.7: Circuits for safety services
To ensure a high-integrity supply and to minimise disruption (electrical faults, maintenance or modification to other systems), a safety service should employ a dedicated independent circuit, that is ideally run through areas of low fire risk.
Where impracticable, a circuit should be run using a fire-resistant cable system.

## Slide 13: Summary
You should now be able to:
Define a safety service and give common examples
Differentiate automatic vs non-automatic sources

## Slide 14
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.