## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.12 Methods of terminating cables
K1.13 Methods of terminating and connecting conductors
PowerPoint 1.12-1.13: Cable termination and conductor connection methods

## Slide 2: Introduction
What do you think makes a good termination?

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain how to terminate and secure different cable types using glands, grips and clamps in line with current standards and specifications
Describe how to connect and terminate conductors using various methods such as screw, crimp, compression, solder and insulation displacement
Apply relevant guidance from BS 7671, manufacturer instructions and Building Regulations when selecting suitable termination and connection methods
Notes: This session builds on prior knowledge of cable types from K1.8. Learners now focus on how those cables are installed safely using the correct support systems. Tutor should reference real-world scenarios, manufacturer examples (e.g. Doncaster Cables or Prysmian), and show physical samples or videos where possible.

## Slide 4: Cable and conductor terminations
Proper termination of cables and conductors is essential for electrical safety, system reliability and compliance with regulations.
There are different methods of terminating cables and conductors, ensuring:
  terminations are fit for purpose, well protected, mechanically and electrically sound, and
  suitable for the environment in which they’re installed.
Notes: This session introduces learners to key termination and connection methods for various cable types and conductor configurations.
Emphasise how improper terminations can lead to failures, overheating, or safety issues. Use real-world examples or show damaged installations to highlight the importance of correct practice.

## Slide 5: Cable glands
Cable glands are mechanical fittings that secure and seal cable entries into enclosures, providing strain relief and environmental protection.
They are essential when terminating SWA, MICC, FP200, and other fixed wiring cables.
Glands must be selected based on cable type, enclosure material, IP rating requirements, and any external influences such as moisture, dust, or chemicals.
Gland kits for SWA cables include a banjo washer for earthing, ensuring electrical continuity of the armour.
Notes: Discuss how incorrect gland selection or poor installation can lead to moisture ingress, mechanical strain, or loss of CPC continuity.
Highlight differences between brass, plastic, and stainless-steel glands and their suitability for indoor, outdoor, or hazardous environments. Demonstrate with a sample SWA/MICC gland kits if available.
https://cableglands.co.uk/

## Slide 6: Termination of MICC cable
MI cable outer sheathing is colour-coded orange for general electrical wiring, white for emergency lighting or red for fire alarm installations.
The copper conductors are embedded in a white powder, magnesium oxide.
This powder is non-ageing and non-combustible, but is hygroscopic, which means that it readily absorbs moisture from the surrounding air, unless adequately terminated.
The termination of an MI cable is a complicated process and requires the electrician to demonstrate a high level of practical skill and expertise.
Notes: Show various glands and pots, in the workshop demonstrate the termination procedure.

## Slide 7: Terminating steel wire armoured cable
To correctly provide the path to earth and securely terminate the cable into an enclosure, correct SWA glands must be used.
BW (internal glands): Suitable for terminations into enclosures where there is no exposure to moisture. For example, connecting to a distribution board inside a commercial unit. BW glands must not be used outdoors or in areas where there is a likelihood that the gland will be exposed to rain/moisture.
CW (external glands): Designed for use outdoors or in other areas where exposure to water is a possibility. These have another rubber ring within the gland which tightens onto the outer sheath of the cable.
Notes: Demonstrate termination of steel by armour.
Have pre-glanded SWA to show with BW gland.
Have pre-glanded SWA to show with CW gland.

## Slide 8: When armour is used as a protective conductor
In some circumstances, the armouring can be used as the protective conductor, as permitted by Regulation 543.2.1. Doing so can result in reduced cable sizes and costs.
However, it must be confirmed that the SWA for the particular cable size is adequate for this purpose. Typically, the CSA of the armouring is sufficient to meet the adiabatic requirements of Regulation 543.1.3.
Where the armour is used as a protective conductor, a separate protective conductor should provide continuity between the accessory's earth terminal and the metallic enclosure (Regulation 543.2.7).

## Slide 9: Armoured/braided cables termination
Armoured or braided flex cable is an industrial, reinforced cable designed to provide control functions in demanding environments where resistance to high levels of stress without a loss of flexibility is required.
Dependent on the installation, the two most common glands used are CX glands and CXT glands.
A CX gland is terminated similarly to other armoured cables, whereas with a CXT gland, the braid is separated into two pigtails.
When the gland is fitted, the pigtails are placed in the slots and are then compressed using the locknut and the gland body.

## Slide 10: Securing cables with grips and clamps
Grips and clamps mechanically secure flexible and fixed cables, preventing strain on electrical terminations. Common types include cord grips in plug tops, cable clamps in junction boxes, and saddle clips on lighting pendants.
These fixings are vital for ensuring the longevity of terminations and compliance with regulations such as strain relief and mechanical protection.
Grips and clamps must be appropriately sized and securely fastened. Where cables enter enclosures or connect to portable appliances, a grip prevents tension from being transferred to the internal connections.
Notes: Explain the importance of preventing mechanical strain on conductors, particularly with flexible cables. Discuss the risk of conductor damage or loose connections without proper grip.
Demonstrate examples using plug tops and flex.
Regulation 522.8.5, which requires suitable strain relief.

## Slide 11: Choosing termination methods for environment
Cable and conductor terminations must be selected based on the environment they will operate in.
This includes temperature, moisture, chemical exposure, UV radiation, and mechanical stress.
Using unsuitable termination methods in harsh conditions can lead to corrosion, water ingress, or failure due to movement or thermal expansion.
Compliance with BS 7671, Building Regulations, and manufacturer specifications is essential for ensuring long-term safety and reliability.
Notes: Discuss typical environments where enhanced protection is needed (e.g. industrial, outdoor, damp).
Compare different materials (e.g. brass vs plastic glands), IP ratings.
Link to Regulation 522.
Demonstrate practical examples (e.g. SWA glands for armoured cables in external settings CW/BW).

## Slide 12: Conductor termination types
Screwed: typical for most electrical sockets and switches
Crimped: secure termination of multistrand conductors
Push wire and lever connectors: non-maintained connection
Soldered: mainly for electronics; less common in fixed wiring
IDC (insulation displacement): used in data/alarm systems.
Each method must suit the conductor and be installed to manufacturer specs and BS 7671 standards.
Notes: Highlight the need for proper tools and torque settings.
Poor termination = a key issue in testing/faults.
Reference BS 7671 Reg 526.3
Demonstrate the difference in termination types, what are their advantages? Disadvantages? Give examples of where and how each is used.

## Slide 13: Maintained vs non-maintained connections
Maintained connections need to be accessible for regular inspection and tightening (e.g. terminals in consumer units).
Non-maintained don’t need regular maintenance or adjustments; connections can be sealed or inaccessible (e.g. resin-filled joints).
Choice of connection depends on:
access for future maintenance
location and environmental factors
cost where both maintained and non-maintained are acceptable.
Notes: BS 7671 Reg 526.3

## Slide 14: Insulation displacement connections (IDC)
IDCs connect conductors by slicing through the insulation, making contact without stripping the wire. A sharp metal blade within the terminal pierces the insulation and makes contact with the conductor.
Common in data cabling and modular connectors (e.g. telephone, Cat5/Cat6).
Provide fast, reliable connections for signal and control circuits.
Notes: Ideal where many fast, repeatable terminations are needed.
Discuss limitations: typically not reused, limited current capacity.
Emphasise correct tooling and cable type (solid core).
Commonly used in data cabling (e.g. RJ45 connectors) and lighting systems.
Must be used with compatible cable types (usually solid conductors).
Not suitable for high-current circuits unless specifically designed for that purpose.
Demonstrate using a Cat5e IDC punch-down on a data outlet module

## Slide 15: Crimped terminations
Crimped terminations involve compressing a metal connector (usually a lug or ferrule) onto a stripped conductor using a crimping tool.
This creates a permanent, mechanically strong and low-resistance electrical connection.
Crimps must be matched to both conductor size and type, and applied with the correct tooling to avoid loose or high-resistance joints, which may overheat or fail.
Notes: Emphasise the importance of using the correct size lug and tool for the cable type.
Highlight the difference between insulated and uninsulated crimp terminals.
Demonstrate a good vs poor crimp.

## Slide 16: Push wire and lever connectors
Push-wire and lever connectors are modern, tool-free connection methods used widely in domestic and commercial installations.
They are designed to provide quick, secure terminations with minimal effort.
Notes: Demonstrate both types of connector in class. Emphasise their ease of use and how they reduce installation time but are more expensive than alternatives.
Push-wire connectors:
Wires are pushed directly into the connector to engage an internal spring clamp.
Single-use: once inserted, wires typically cannot be removed without damage.
Lever connectors:
Reusable and ideal for maintenance, testing, or temporary setups.
Feature a small lever to open and close the clamping mechanism.
https://www.wago.com/global/installation-terminal-blocks-and-connectors/splicing-connector-with-levers/p/221-412#details

## Slide 17: Soldered terminations
Soldered connections are made by melting solder around the conductor and terminal to create a solid electrical and mechanical joint.
Provides excellent conductivity and is commonly used in low-voltage electronic circuits.
But is less typical in fixed wiring systems.
Notes: Emphasise that soldered joints are more relevant in electronics than fixed installation work.
Ask learners if they’ve seen soldering used in the field and under what circumstances.

## Slide 18: Summary
You should now be able to:
Explain how to terminate and secure different cable types using glands, grips and clamps in line with current standards and specifications
Describe how to connect and terminate conductors using various methods such as screw, crimp, compression, solder and insulation displacement
Apply relevant guidance from BS 7671, manufacturer instructions and Building Regulations when selecting suitable termination and connection methods

## Slide 19
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.