## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.14 Inspections for initial verification of electrotechnical systems
PowerPoint 1.14: Standard procedures and processes to undertake inspections
Notes: https://electrical.theiet.org/wiring-matters/years/2025/105-may-2025/minimizing-unnecessary-live-testing-for-initial-verification/
https://electrical.theiet.org/wiring-matters/years/2019/78-november-2019/fire-stopping/

## Slide 2: Introduction
Why is the inspection of a new electrical installation completed before testing can commence?

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain the purpose of initial verification and where it fits in the commissioning process
Identify the key items to be visually inspected in accordance with BS 7671 and IET Guidance Note 3
Recognise the required documentation for compliance, including the Electrical Installation Certificate and schedules

## Slide 4: What is initial verification?
Initial verification is the process of confirming that a new electrical installation complies with BS 7671 before it is energised.
It involves a combination of inspection and testing to ensure the installation is safe, correctly installed and suitable for operation.
This must be completed before the installation is put into service and includes visual checks, electrical tests and documented evidence.
Notes: Initial verification is a mandatory process for all new installations and significant alterations.
Stress that this is before energisation and forms part of the commissioning process. Link to Regulation 641.1 of BS 7671 of EAWR.
Regulation 14: Prohibits working on live conductors unless absolutely necessary and safe precautions are in place.
Regulation 16: States that only competent individuals with appropriate training should carry out inspection and testing work.

## Slide 5: Requirements for electrical installation inspection
Three main requirements for the inspection process during initial verification.
The equipment installed complies with Regulation 511.1, page 130.
The installation is correctly selected and erected in accordance with BS 7671, taking into account the manufacturer’s instructions (Regulation 642.2, page 232).
The installation is not visibly damaged or defective to impair safety (Regulation 642.2, page 232).
The inspection should include checking all relevant items listed in Regulation 642.3 on page 232 of BS 7671.

## Slide 6: IET Guidance Note 3: Inspection & Testing
Guidance Note 3 explains in further detail the testing process and requirements of Part 6 of BS 7671.
The book details all the testing procedures for both initial and periodic testing.
It also details the test instrument requirements and the necessary documentation to be completed.
Notes: Introduce the learners to Guidance Note 3: Inspection & Testing published by the IET.
Explain that this book is designed to expand on Part 6 of BS 7671, which deals with inspection and testing requirements for electrical installations.
Show a physical copy of the book if available and explain the value of referencing it when preparing for assessments or real-world work.

## Slide 7: Refer to the general requirements given in IET GN3
Section 1 of GN3 refers to:
the safety measures of undertaking an electrical inspection
the required competence of the inspector
general information on the appropriate processes.
Section 1: General requirements
Section 2: Initial verification
Section 3: Periodic inspection and testing
Section 4: Test instruments and equipment
Section 5: Form
Notes: Direct learners to Section 1 of GN3, titled General requirements. This section sets out essential safety practices and the responsibilities of the inspector.
Point out the importance of competency in those carrying out inspections, including understanding equipment, safety procedures, and record keeping.

## Slide 8: Required information
GN3 requires that the following information be made available to the person or persons carrying out the inspection process.
Section 2.3, page 23
The maximum demand, expressed in amperes per phase (after diversity is taken into account).
The number and type of live conductors of the source of energy and of the circuits used in the installation.
The type of earthing arrangement used by the installation and any facilities the supplier provides for the user.

## Slide 9: Required information: continued
The nominal voltage(s).
The nature of the load current and supply frequency.
The prospective fault current at the origin of the installation.
The earth fault loop impedance (Ze) of that part of the system external to the installation.
The suitability of the installation requirements, including maximum demand.
The type and rating of the overcurrent protective device acting at the origin of the installation.
Notes: Reinforce the point that this information must be verified before testing or energising.

## Slide 10: What does an inspection involve?
Focuses on a thorough visual and physical examination of the installation:
correct routing of cables
proper support and fixing
compliance with IP ratings
accessibility of isolation devices
identification and labelling
selection of correct devices.
It also ensures no damage or defects are visible prior to testing.
Notes: Refer to BS 7671 Section 641 and Guidance Note 3, Chapter 2. Discuss that this stage does not involve any test instruments, it is entirely visual and tactile.

## Slide 11: Typical items inspected during initial verification
Presence of main and supplementary bonding.
Correct identification of conductors (e.g. colours, marking).
Correct selection of protective devices.
Labelling of DBs and final circuits.
Accessibility for maintenance and isolation.
Fire-stopping in penetrations.
Securely fixed wiring systems.
Notes: Use GN3 section 2.5.2 comments on individual items to be inspected.
Use PB7671 Reg 642
Encourage learners to visually assess installations, show examples of items to be inspected which do not meet standards.
https://electrical.theiet.org/wiring-matters/years/2020/79-march-2020/getting-important-labelling-right-leaves-a-lasting-impression/

## Slide 12: Using inspection checklists effectively
Initial verification should be guided by structured documentation such as visual inspection checklists (like those in IET GN3 or EIC forms).
Checklists reduce the risk of missed steps and ensure consistent standards.
Example:
Item No. | Description | Outcome  / N/A
1.0 | Condition of consumer’s intake equipment (Visual inspection only) | 
2.0 | Parallel or switched alternative source of supply | 
Notes: https://electrical.theiet.org/bs-7671/model-forms/

## Slide 13: Referencing BS 7671 and GN3 during inspection
During inspection, both BS 7671 (Regulations) and IET Guidance Note 3 (GN3) must be used to determine whether the installation complies with current standards.
BS 7671 outlines the legal and technical requirements (e.g. Regulation 514 for identification, 522 for wiring methods).
GN3 provides practical visual checklists and recommended procedures for inspections and documentation.
Notes: Reinforce that these two documents must be used together. GN3 is essential for planning inspections and understanding what to look for. Mention that BS 7671 describes what must be done, GN3 helps with how.

## Slide 14: Recording and documenting inspections
Inspection findings must be recorded clearly on the Electrical Installation Certificate (EIC) and supporting schedules, including a checklist of inspected items.
Details of any departures from the standards must be justified and recorded.
Documentation ensures traceability and accountability and provides a reference for future maintenance or alterations.
Notes: Explain that these documents are legally important and must be retained.

## Slide 15: Information required by Regulation 514.9.1: pg. 135
A diagram, chart or table or equivalent form of information shall be provided indicating in particular:
the type and composition of each circuit (points of utilisation served, number and size of conductors, type of wiring)
the method used for compliance with Regulation 410.3.2
the information necessary for the identification of each device performing the functions of protection, isolation and switching, and its location
any circuit or equipment vulnerable to the electrical tests as required by Part 6.

## Slide 16: Chapter 64 Reg: 644.1, page 238
An Electrical Installation Certificate shall be issued to the person ordering the work:
upon completion of the verification of a new installation
or an addition or alteration to an existing installation, including the replacement of a distribution board or consumer unit.
Notes: Show the various forms to learners: https://electrical.theiet.org/courses-resources-and-career/forms-and-downloads/

## Slide 17: The role of documentation
After initial verification, test results and inspection records must be kept.
Electrical Installation Certificate (EIC): Confirms the installation is safe to be put into service.
Schedule of Test Results: Lists all tests carried out and their results.
Inspection Checklist: Records visual checks and compliance with BS 7671.
These records provide proof that the installation meets the design criteria and complies with safety regulations.

## Slide 18: O&M manuals and handover documentation
As part of the initial verification and commissioning process, Operation & Maintenance (O&M) manuals must be provided to the client.
These include as-fitted drawings, schedules, circuit identification, manufacturers’ data sheets and maintenance instructions.
Providing this documentation ensures the system can be operated and maintained safely.
Notes: Tie this back to BS 7671 Regulation 514.9 and Guidance Note 3. Emphasise the importance of providing clear, usable information to the building owner or operator. This forms part of the completion and compliance process.

## Slide 19: Summary
You should now be able to:
Explain the purpose of initial verification and where it fits in the commissioning process
Identify the key items to be visually inspected in accordance with BS 7671 and IET Guidance Note 3
Recognise the required documentation for compliance, including the Electrical Installation Certificate and schedules

## Slide 20
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.