## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.15 Testing for electrotechnical systems
PowerPoint 1.15: Polarity

## Slide 2: Introduction
Why is it dangerous if the neutral and line conductors are reversed at a socket outlet, even if the device still works?

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain the purpose of polarity testing and when it is applied
Carry out polarity tests using approved methods and instruments
Describe live and dead polarity test procedures
State appropriate PPE and safety procedures when testing live systems

## Slide 4: Why it is necessary to verify polarity
Test with the supply disconnected
All single pole devices and protective devices connected to line conductor only.
Edison screw lamp holders have the centre point connected to line conductor.
Wiring has been correctly connected to socket outlets and similar accessories throughout the installation.
Test with the supply connected
To ensure the incoming tails have been correctly connected.
Notes: GN3 Section 2, 2.6.12,page 78
BS7671 Chapter 64, 643.6, page 235

## Slide 5: The procedure for verifying polarity
This test can be undertaken using the same methods used for measuring continuity of CPC, via test method 1 or test method 2 as shown previously. (In reality, this procedure is done at the same time).
We use the same process for any radial circuit, lighting, socket outlets, etc. Polarity can also be confirmed using a visual inspection.
Polarity testing of ring final circuits is automatically done as we progress through steps 1–3 of the continuity of ring circuit procedures.

## Slide 6: Figure 2.27 from guidance note 3
A polarity test carried out on an Edison screw lamp holder requires the inspector to prove the polarity of the centre pin in the lamp holder.
Notes: See IET image: Figure 2.27 from guidance note 3.

## Slide 7: Polarity tests with the supply disconnected
Polarity Method 1 Using the continuity/ohm scale on the instrument and with the plate switch in the 'off' position and the MCB closed, the reading should be infinite, then with the switch closed, there should be a resistance value.
This verifies that the switch and the MCB is connected to the line conductor only.
The actual value is irrelevant as long as there is a value when the switch is on and no value when the switch is off.

## Slide 8: Polarity: Method 2
Using the continuity/ohm scale on the instrument and with the plate switch in the 'off' position and the MCB closed, the reading should be infinite, then with the switch closed, there should be a resistance value.
This verifies that any switches and protective devices are connected to the line conductor only.
The actual value is irrelevant as long as there is a value when the switch is on and no value when the switch is off.
Notes: Note: method two is rarely used as polarity is normally confirmed whilst testing continuous CPC.

## Slide 9: The procedure for verifying LIVE polarity
Test with the supply connected to ensure the incoming tails have been correctly connected.
This is done using an approved voltage indicator at the main isolator switch.
The voltages between the conductors are checked and verified for correctness.
L–N = 230 volts N–E = 0 volts
L–E = 230 volts L-L = 400 volts

## Slide 10: Summary
You should now be able to:
Explain the purpose of polarity testing and when it is applied
Carry out polarity tests using approved methods and instruments
Describe live and dead polarity test procedures
State appropriate PPE and safety procedures when testing live systems

## Slide 11
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.