## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.15 Testing for electrotechnical systems
PowerPoint 1.15: Requirements for electrical testing

## Slide 2: Introduction
Why do you think tests must be carried out in a specific sequence during initial verification?

## Slide 3: Objectives
By the end of this session, you should be able to:
Identify the types of tests required during electrical inspection and initial verification
Explain why tests must be conducted in a specific order according to BS 7671 and IET Guidance Note 3
Use appropriate test instruments safely, including PPE requirements
Check test equipment for functionality, accuracy, and compliance with GS38

## Slide 4: Safe and correct use of measuring instruments
Equipment should be:
constructed
maintained
used in a way to prevent danger.
Users should have the knowledge they need to use and maintain equipment safely.

## Slide 5: Test equipment
The use of test equipment by electricians falls into three main categories:
testing for voltage (voltage detection)
measuring voltages
measuring current, resistance.
Item 1: Essential part of the procedure for proving a system dead before starting work but may also be associated with simple tests to prove the presence of voltage.
Items 2 and 3: More concerned with commissioning procedures and fault finding.

## Slide 6: Tests when completing initial inspection
A sequence of tests needs to be undertaken following the completion of an installation.
Items listed a) to n) need to be completed, where practicable, in that order.
When conducting an initial verification on a new circuit/installation, any test on a circuit failing the expected normal outcomes should be stopped and the fault rectified before testing can continue.
The tests listed are not relevant to all circuits/installations. The inspector should identify those that need to be undertaken.

## Slide 7: Sequence of tests
(a) continuity of protective conductors, including main and supplementary bonding (see Section 2.6.5) (Regulation 643.2.1)
(b) continuity of ring final circuit conductors (see Section 2.6.6) (Regulation 643.2.1)
(c) insulation resistance (see Section 2.6.7) (Regulation 643.3)
(d) protection by SELV, PELV or by electrical separation (see Sections 2.6.8 and 2.6.9) (Regulations 643.4, 643.4.1, 643.4.2)
(e) insulation resistance of non-conducting floors and walls (see Section 2.6.11) (Regulation 643.5)
(f) polarity (Section 2.6.12) (Regulation 643.6)

## Slide 8
(g) protection by ADS (Section 2.6.15) (Regulations 643.7, 643.7.1, 643.7.2, 643.7.3)
(h) earth electrode resistance (Section 2.6.13) (Regulation 643.7.2)
(i) EFLI (Section 2.6.15) (Regulation 643.7.3)
(j) prospective fault current (Section 2.6.16) (Regulation 643.7.3.201)
(k) additional protection(Section 2.6.18) (Regulation 643.8)
(l) Check of phase sequence (Section 2.6.17) (Regulation 643.)
(m) functional testing (Sections 2.6.18 and 2.6.19) (Regulation 643.10)
(n) verification of voltage drop (Section 2.6.20) (Regulation 643.11).

## Slide 9: Why testing is carried out in the sequence specified
Many tests rely on the results of certain other tests being correct.
Any test that fails to produce an acceptable result must be repeated after remedial action has been taken.
Any other tests, whose results may have been influenced by the fault concerned, must also be repeated.

## Slide 10: Safe systems of work
It's vital to follow a clear and safe procedure before starting any electrical testing, whether during initial verification or a periodic inspection.
Carry out a risk assessment for the task.
Identify and apply safety precautions.
Ensure safe isolation of the circuit or system.
Use test instruments that are suitable and in working condition.
Communicate with clients or others affected by the work.
Understand the capabilities and limitations of the test methods used.
Consider how the work might affect others in the environment.

## Slide 11: Dead tests
Below are the common tests undertaken before the supply is connected.
Continuity of protective conductors, including main and supplementary bonding (643.2)
Continuity of ring final circuit conductors (643.2)
insulation resistance (643.3)
Polarity (643.6)
Notes: BS7671 Chapter 64, pages 234+

## Slide 12: Live tests
Below are the common tests undertaken with the supply connected.
Confirmation of supply polarity.
Protection by automatic disconnection of the supply.
Earth fault loop impedance Ze and Zs.
Prospective fault current measurement.
Phase sequence.
Functional testing, including RCDs and switchgear.
Verification of voltage drop.
Notes: BS7671 Chapter 64, pages 235+
GN3 Section 2, 2.6.4, page 56

## Slide 13: Reasons for test results to comply
When inspecting installations, our objective is to make sure that it is safe to use, meets the design specifications and is fit for purpose. It must also meet the requirements of BS 7671.
Every installation shall be inspected and tested during erection and on completion before being put into service to verify, so far as is reasonably practical, that the regulations' requirements have been met.
Test results must comply with industry values because they verify that the installation meets the criteria for protection against electric shock.
Notes: BS7671 Chapter 64, Reg: 641.1 Reg: 642.2, page 232.
GN3 Section 2, 2.1, page 21.

## Slide 14: Inspection of installed electrical equipment
The inspection shall be made to verify that the installed electrical equipment is:
in compliance with the requirements of Section 511
correctly selected and erected in accordance with the regulations, taking into account the manufacturer’s instructions
not visibly damaged or defective to impair safety.
In the event of any inspection or test not meeting the requirements, testing should stop, then the fault should be rectified and the circuit retested to assess compliance with BS 7671.

## Slide 15: Testing of continuity of protective conductors
We can be certain that in the event of a fault, enough fault current will flow to operate the protection device within the maximum disconnection times given by:
testing of continuity of protective conductors, insulation resistance, Zs, etc, and
comparing the results with BS 7671.
This will reduce the time the fault is present, reducing the risk of shock and fire.

## Slide 16: Actions when unsatisfactory results are obtained
If any test shows a failure to comply:
that test shall be repeated after the fault has been rectified
any preceding test that may have been influenced by the fault shall also be repeated.

## Slide 17: Checking and calibrating test instruments
Test instruments are essential for ensuring electrical installations are safe and meet BS 7671 regulations. All test instruments must be regularly checked and calibrated.
Check the test leads for damage (no cuts, cracks, or exposed wires).
Ensure test probes meet GS38 safety standards for circuits over 50V AC.
Check and replace batteries if needed - Low battery power can cause incorrect readings.
Before use, test leads should be zeroed to eliminate errors in resistance readings.
Instruments should be professionally calibrated at n accordance with the manufacturer’s instructions taking usage into account.

## Slide 18: Low-resistance ohmmeters
The instrument used for low-resistance tests may be either a specialised low-resistance ohmmeter or the continuity range of an insulation and continuity tester.
The test current may be DC or AC. It is recommended that it be derived from a source with a no-load voltage between 4V and 24V and a current not less than 200mA.
For digital instruments, the measuring range should cover the span 0.2 ohm to 2 ohms, with a resolution of at least 0.01 ohm. This means that the instrument can measure in increments of 1/100th of an ohm.
Notes: The basic instrument standard is BS EN 61557. When inspecting electrical installations within the voltage bands of low voltage distribution systems up to 1,000V AC and 1,500V DC, all test instruments/equipment used must comply with this standard.
643.1 Measuring instruments and monitoring equipment and methods shall be chosen in accordance with the relevant parts of BS EN 61557. If other measuring equipment is used, it shall provide no lesser degree of performance and safety.

## Slide 19: Insulation resistance meter
The instrument used should be capable of developing the test voltage required across the load.
250V DC for SELV and PELV circuits
500V DC for all circuits rated up to and including 500V, but excluding extra-low voltage circuits mentioned above
1,000V DC for circuits rated above 500V up to 1,000V.
The tester must be capable of supplying an output current of 1mA at the required test voltage.

## Slide 20: Earth fault loop impedance testers
These instruments operate by circulating a current from the line conductor into the protective earth. This will raise the potential of the protective earth system.
For circuits rated up to 50A, a phase-earth loop tester with a resolution of 0.01 ohm should be adequate.
Instruments conforming to BS EN 61557-3 will fulfil the above requirements.
These instruments may also offer additional facilities for measuring prospective short-circuit currents.

## Slide 21: RCD testers
The test instrument should be capable of applying the full range of test current to an in-service accuracy as given in BS EN 61557-6.
This in-service reading accuracy will include the effects of voltage variations around the nominal voltage of the tester.
To check RCD operation and to minimise danger during the test, the test current should be applied for no longer than two seconds (>1999mSeconds).

## Slide 22: Identifying the correct scale or setting
When measuring resistances, we need to use the ohm scale.
When measuring insulation resistance, we need to use the meg ohm scale and set the voltage at the necessary level for the circuit being tested.
When measuring earth loop impedance, it would be set on the loop (ohm) range.
When measuring prospective fault current, the instrument would be set on both the loop (L–E) and line (L–N) settings, and the current values would be read from the instrument. Values will be documented in kilo amps; 500 amps would be 0.5kA.

## Slide 23: Checks for test instruments
Checks are required to prove that test instruments are safe and functioning correctly.
Before use, visually check that both the instrument and the test leads are in good order. Calibration certificates and expiry dates should also be checked.
Any leads used on circuits above 50V AC need to be of a GS38 standard, and they should be checked for cracks or damage before use.
If any instrument seems damaged or not maintained in good order, it should be removed from service and checked for accuracy/repair.

## Slide 24: Calibration
It is not a requirement to have instruments calibrated on an annual basis.
However, a record must be kept to show that the instruments are regularly checked for accuracy and good condition.
If an instrument requires recalibration for any reason, it should be returned to the manufacturer or a calibration specialist.
Notes: GN3 Section 4, 4.2, page 138.

## Slide 25: HSE Guidance GS38
Before using any test leads, including any probes or clips, ensure they are in good order, are clean and have no cracked or broken insulation.
Where appropriate, the guidance given in GS38 should be observed for test leads.
Notes: This is a free download from the HSE.GOV.UK website:
www.hse.gov.uk/pubns/priced/gs38.pdf

## Slide 26: The requirements GS38
Are adequately insulated (choice of insulating material may be influenced by the environment in which the leads are to be used).
Are coloured so that one lead can be easily distinguished from the other.
Are flexible and of sufficient capacity for the duty expected of them.
Are sheathed to protect against mechanical damage.
Are long enough for the purpose, while not too long so that they are clumsy or unwieldy.
Notes: GN3 Section 4, 4.1, page 137
The HSE always advises only to carry out live tests that are actually useful and informative, so as to minimise danger. The inspector should always consider whether any particular live test is necessary before undertaking it.
The safety measures and procedures set out in GS38 should be observed for all instruments, leads, probes and accessories.

## Slide 27: PPE when conducting live testing
When conducting electrical testing, wearing the appropriate PPE is essential to ensure safety.
The risks associated with electrical live testing:
arc flashes
electric shocks and burns.
These are significantly higher risks in commercial and industrial power systems due to their larger voltage and current levels.

## Slide 28: PPE when conducting live testing
Always ensure your PPE is rated for the voltage level and is regularly inspected for damage before use.​
​Arc Flash Visor: Shields the face and eyes from arc flash incidents and electrical explosions. Rated for voltage level 1000v.​
​LV Insulated Gloves: Protect against electric shock when handling live components. Rated for voltage level 5000v.​​
Electrical safety mat: Provide insulation from the ground, reducing the risk of electrocution. Rated for voltage level 10000v.
Notes: Use this session to reinforce proper PPE for live testing and arc flash awareness.

## Slide 29: Summary
You should now be able to:
Identify the types of tests required during electrical inspection and initial verification
Explain why tests must be conducted in a specific order according to BS 7671 and IET Guidance Note 3
Use appropriate test instruments safely, including PPE requirements
Check test equipment for functionality, accuracy, and compliance with GS38

## Slide 30
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.