## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.15 Safe isolation procedure
PowerPoint 1.15: Safe isolation
Notes: https://electrical.theiet.org/media/1606/safe-isolation-of-low-voltage-installations.pdf

## Slide 2: Introduction
Why is it important to safely isolate an electrical circuit before working on it?
Notes: Discuss the importance of maintaining safe work practices and responsibilities of everyone under the health and safety at work act 1974.

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain when safe isolation is required and its legal basis (Electricity at Work Regs)
Identify the correct point(s) of isolation, including additional sources on prosumer systems (PV, batteries, generators)
Select and check a GS38-compliant approved voltage indicator and a proving unit
Apply the safe-isolation sequence

## Slide 4: Electrical hazards
Most hazards can be:
seen
felt
heard.
There are no second chances with electricity.
ELECTRICITY CAN KILL INSTANTLY.
Notes: Compliance with the EWR 1989 is a legal requirement.
Regulations that are deemed ‘absolute’ must be met irrespective of time or money; others may be deemed ‘reasonably practicable’.
The EWR specifies that ‘employers must recognise different levels of responsibility and adjust supervision accordingly’.
Unqualified employees such as an apprentice should therefore not be left unsupervised.
This means should an electrical apprentice electrocute a client, then the employer will be in breach of vicarious liability.
To avoid this, electrical companies need to adopt safe isolation procedures.
It is imperative that all employees are conversant with this process.
The EWR specifies that ‘working on or near live conductors can only be carried out when it is unreasonable to work “dead” and suitable precautions are in place’.
This means failure to justify why such work was being undertaken and/or failure to put in place suitable safety measures could lead to prosecution.
  The EWR specifies that ‘the means of disconnection must be secured in the OFF position, with a warning notice or label at the point of disconnection, and proved “dead” at the point of work with an approved voltage indicator’.
  This means failure to securely lock off a supply, or prove that the supply is dead through appropriate equipment, could lead to prosecution.

## Slide 5: Electrical isolation
Isolation is defined as ‘removing all forms of energy from a circuit including batteries and charged devices such as capacitors’. Special care must be taken with the advent of prosumer installations (installations that both consume and generate electricity).
In other words, solar panels will still generate electricity during sunny days, and battery storage units can discharge.
In such cases, isolating must therefore be involved:
between PV panels and the inverter
storage batteries, if present
consumer unit.
AI image

## Slide 6: Safe isolation
Safe isolation kits are available to buy, which can securely lock off a number of devices such as:
circuit breakers
fuses (fuse carriers)
main switches.
Notes: To ensure compliance with the EWR, electrical installation companies must incorporate a method statement, referred to as a Safe Isolation Procedure, before any work is carried out.
The isolation system will depend on whether it is an individual circuit or a number of circuits.
Isolation is sometimes referred to as locked off, but this could, in some circumstances, be called disconnecting or even unplugging.

## Slide 7: Safe isolation: Multi-lock hasp
Where a number of trade people require isolation, then a multi-lock hasp must be used.
A typical hasp can cater for six people, each with their own padlock and unique key.
The supply remains isolated until all six people are contented.
Notes: To ensure compliance with the EWR, electrical installation companies must incorporate a method statement, referred to as a Safe Isolation Procedure, before any work is carried out.
The isolation system will depend on whether it is an individual circuit or a number of circuits.
Isolation is sometimes referred to as locked off, but this could, in some circumstances, be called disconnecting or even unplugging.

## Slide 8: Approved voltage tester GS38 compliant
Approved voltage detectors:
are adequately insulated
have leads coloured to differentiate
have finger guards to stop inadvertent hand contact
have spring-loaded tips or are not exposed more than 4mm (optimally 2mm)
are flexible and robust
are sufficiently long.
Notes: https://www.alertelectrical.com/media/productattachment/0/5968/gs38.pdf
https://www.hse.gov.uk/pubns/priced/gs38.pdf

## Slide 9: Proving unit
Prior to testing, the effectiveness of a voltage detector must be established.
This can be done with either:
  a proving unit (d.c. voltage source)
  a known fixed supply, such as the mains.
  A proving unit is always preferable.

## Slide 10: Safe isolation procedure
Carry out a risk assessment and obtain permission to isolate.
Identify the circuit/distribution to be isolated.
Shut off, lock off.
Keep the key on your person.
Test the voltage indicator on a known live source or a proving unit.
Check circuit is dead. L-N, L-E, N-E, L-L
Re-test the voltage indicator.
Put out barriers and signs.
Notes: Gaining permission from the client/customer is essential, not only to stop them from being inconvenienced when the supply is removed without warning.
An electrician has a duty of care towards their client, fellow employees as well as their employer.
Ignorance or mistaking the law is no defence to a criminal charge.
Inconveniencing a client will do nothing for future business.

## Slide 11: Summary
You should now be able to:
Explain when safe isolation is required and its legal basis (Electricity at Work Regs)
Identify the correct point(s) of isolation, including additional sources on prosumer systems (PV, batteries, generators)
Select and check a GS38-compliant approved voltage indicator and a proving unit
Apply the safe-isolation sequence

## Slide 12
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.