## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.10 Types of lighting and luminaire
PowerPoint 1.10: Lighting types, lamp technology and illumination design

## Slide 2: Introduction
What do you think is the most common energy-efficient lamp used today, and why do you think it’s so widely adopted?

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain how the height and spacing of luminaires affect illumination levels
Compare different lighting types and luminaires based on efficacy, energy efficiency, lumens, and colour rendering
Apply the lumen method to estimate lighting requirements in a given space

## Slide 4: What is illumination and why does it matter?
Illumination refers to the amount of light falling on a surface, measured in lux (lx). Good lighting ensures safe, comfortable, and effective working or living conditions.
In electrotechnical installations, lighting must be designed to meet both functional and legal requirements.
Whether for domestic, commercial, or industrial use, the type of lighting system installed directly affects energy use, visibility, mood, and compliance.
Notes: Emphasise that lux is a unit of illuminance (lumens per square metre).
Link to real-world examples (e.g. lux in corridors vs lux at a desk).
Use a lux meter in class if possible, or a demo app on a phone.
https://mountlighting.co.uk/technical/cibse-recommended-lighting-levels/
https://www.gov.uk/government/publications/conservation-of-fuel-and-power-approved-document-l

## Slide 5: Understanding the lumen and lux relationship
Lumen (lm) measures the total amount of visible light emitted by a source.
Lux (lx) is how much of that light reaches a surface.
One lux is equal to one lumen per square metre. A bright lamp in a small room produces a high lux level, but the same lamp in a large room may not give enough light for tasks. This is why both the number of lumens and the distribution of light matter are important when designing lighting installations.
Notes: Reinforce: Lumen = output, Lux = light received
Bring a lux meter to class or use a mobile app for practical demonstration.
Link to manufacturer data sheets showing lumens and coverage.

## Slide 6: Why mounting height affects illumination
The higher a luminaire is mounted, the further its light has to travel and the lower the light level that reaches the working plane.
This is due to the inverse square law, which states that light intensity decreases rapidly as distance increases.
Raising the height can improve light spread but reduces lux levels unless higher-output fittings or more luminaires are used.
Designers must balance coverage and intensity when deciding on mounting height.
Notes: Cover the inverse square law: E = I / d²
Show how mounting height and beam angle affect lux distribution.
Use flashlight demo across different heights.

## Slide 7: Luminaire spacing
Spacing between luminaires affects how evenly light is distributed across a space.
If luminaires are too far apart, there will be dark patches or shadows. If placed too close together, the spaces may be over-lit, leading to energy waste.
A good design ensures uniform illumination that meets the lux levels required for the room’s function.
Notes: Relate to practical scenarios — e.g. corridors, car parks, workshops.
What could go wrong with uneven lighting?
Talk about using manufacturers data sheets.
https://assets.cef.co.uk/downloads/pdg/tamlite_hrc66450nw_datasheet/tamlite_hrc66450nw_datasheet.pdf

## Slide 8: Beam angles
Light beam angles control how a fixture distributes its illumination, whether you’re lighting up an entire space or accentuating a particular feature.
40°beams are the go-to choice for general room lighting in most homes when fixtures are mounted on the ceiling.
90°beams work best for outdoor spotlights, where a wider spread helps light up a wider area.
Notes: https://www.downlightsdirect.co.uk/advice/downlights/which-beam-angle-to-choose/

## Slide 9: Understanding lumens and efficacy
Lumens (lm) measure the amount of visible light a lamp produces. The higher the lumens, the brighter the light.
Efficacy is the lamp’s efficiency, measured in lumens per watt (lm/W). It tells us how much light is produced for every unit of electrical power consumed. A lamp with high efficacy uses less energy to produce the same light output.
Example
A 10W LED produces 1000 lumens = 100 lm/W
A 60W incandescent bulb produces 800 lumens = 13 lm/W

## Slide 10: Colour rendering and appearance
The Colour Rendering Index (CRI) measures how accurately a light source shows object colours compared to natural daylight.
The scale runs from 0 to 100.
The higher the CRI, the more natural colours appear.
A CRI of 80+ is acceptable for most general applications.
90+ is ideal where colour accuracy is critical (e.g. art studios, medical).
Notes: https://www.nultylighting.co.uk/blog/what-is-colour-rendering-index-cri-lighting/

## Slide 11: Correlated Colour Temperature (CCT)
Correlated Colour Temperature (CCT) describes whether the light appears warm or cool.
2700K-3000K = warm white (yellowish, cosy feel)
4000K = cool white (neutral, offices)
6000K+ = daylight (bluish, industrial)
Choosing the correct CRI and CCT ensures both comfort and accurate visibility in the space.
Notes: Talk about LED lights on the availability of different colour temperatures
Which LEDs would be suitable for kitchens, lounges, and home offices?

## Slide 12: Low-pressure mercury vapour lamps
Commonly known as fluorescent lamps.
These lamps were widely used in commercial settings but are being phased out in favour of more efficient and environmentally friendly options like LEDs.
As of February 1, 2024, the UK has banned the sale of most fluorescent lamps, including T5, T8, and compact fluorescent lamps (CFLs).
Note: These contain mercury and are classified as hazardous waste. Proper disposal is required.
Notes: https://www.hse.gov.uk/waste/waste-electrical.htm
https://www.gov.uk/government/publications/restriction-of-hazardous-substances-rohs-determinations-on-exemption-applications/rohs-exemption-applications-secretary-of-state-determinations

## Slide 13: Halogen lamps
Halogen lamps were once widely used in homes, particularly in bathrooms, kitchens and display lighting due to their compact size and bright, white light.
However, halogens are now being phased out following the government’s ban in September 2021, due to their poor energy efficiency compared to LED alternatives.
Notes: https://www.gov.uk/government/news/end-of-halogen-light-bulbs-spells-brighter-and-cleaner-future
Discuss replacement options and typical retrofitting to LED GU10s or MR16s in practice.

## Slide 14: LEDs
Light Emitting Diodes (LEDs) are now the dominant form of lighting across domestic, commercial and industrial environments.
LEDs convert electrical energy directly into light with minimal heat loss, making them far more efficient than traditional lamps.
LEDs offer long life spans, low running costs and instant full brightness.
They are available in a wide range of colour temperatures and can be dimmed or controlled via smart systems. Their compact size allows for creative luminaire designs.
Notes: https://www.hse.gov.uk/waste/waste-electrical.htm

## Slide 15: Smart lighting
Smart lighting allows lights to be controlled automatically or remotely using apps, sensors, or timers.
It can adjust brightness and colour based on time of day, occupancy or natural light.
This helps improve comfort and energy efficiency in homes, offices, and industrial spaces.
Notes: https://www.hse.gov.uk/waste/waste-electrical.htm

## Slide 16: Cosine law
The cosine law is used to calculate how much lux is produced by a lamp in proportion to a given angle.
If the angle is given in degrees, then use the Cos function:
Cos 37.5° = 0.79
∅

## Slide 17: Example
How much illuminance is produced at point A if the illuminance intensity is 2,000 candela?
Cos 35°= 0.82
35°
2m

## Slide 18: The lumen method
The lumen method is a calculation used to estimate the average illuminance (lux) within a space, based on the total light output from luminaires.
It is often used during lighting design to ensure the area meets required lighting levels for tasks or regulations.
This method works best for spaces with uniform lighting and surfaces, such as classrooms, offices or workshops.
It does not account for shadows or directional lighting but provides a reliable estimate of general light levels.
Notes: BS EN 12464-1:Light and lighting. Lighting of work places - Indoor work places

## Slide 19: The lumen method
Using the lumen method to calculate the overall illumination level for a square or rectangular room:
E = average illumination
F = average flux from each lamp
N = number of lamps required
MF = maintenance factor (accounts for lamp ageing and dirt)
UF = utilisation factor (based on room shape and reflectance)
A = area

## Slide 20: Example
A workshop has an area of 40 m² and uses 4 luminaires, each producing 3,000 lumens. The utilisation factor is 0.6 and the maintenance factor is 0.8.
This means the space will have an average illuminance of 144 lux.
Notes: https://www.hse.gov.uk/humanfactors/topics/lighting.htm
Discuss whether this is an acceptable illuminance.
https://www.any-lamp.com/blog/european-standard-nen-124641?switch=2068741841078121120

## Slide 21: Summary
You should now be able to:
Explain how the height and spacing of luminaires affect illumination levels
Compare different lighting types and luminaires based on efficacy, energy efficiency, lumens, and colour rendering
Apply the lumen method to estimate lighting requirements in a given space

## Slide 22
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.