## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.6 Special installations and locations specified in national standards
PowerPoint 1.6: Special locations16 Equipment adjustments as required by installation standards to ensure correct function

## Slide 2: Introduction
Why do you believe there is a need for extra regulations for special locations such as caravan parks on swimming pools?

## Slide 3: Objectives
By the end of this session, you should be able to:
Explain why Part 7 exists and how it adds to Parts 4-6 for higher-risk locations
Identify the BS 7671 Part 7 sections relevant to typical sites
Recognise when the work is beyond non-specialist competence

## Slide 4: Part 7: Why it exists
Some places/environments pose higher risk; they need extra rules on top of Parts 4-6.
Part 7 gives location-specific requirements for design, installation, inspection & testing.
Always apply the general rules first, then add the relevant Part 7 section.
Competence matters: certain locations (e.g. medical, marinas, EV, pools/saunas, fairgrounds) may require specialist training/experience beyond a standard qualification.
Notes: Some places/environments pose higher risk → they need extra rules on top of Parts 4–6.
Part 7 gives location-specific requirements for design, installation, inspection & testing.
Always apply the general rules first, then add the relevant Part 7 section.
Competence matters: certain locations (e.g. medical, marinas, EV, pools/saunas, fairgrounds) may require specialist training/experience beyond a standard qualification.

## Slide 5: Special installations and locations as identified in Part 7 of BS 7671
There are many areas where we have to identify that there may be higher risks to the user.
BS 7671 lists special installations or locations where we need to ensure:
additional protection or
specialised equipment or
additional installation processes.
Notes: This list is taken from the BS 7671 contents. For each section, start with GN7; add GN1/GN2/GN3/GN5/GN8 as needed for device selection, isolation, testing, shock protection and bonding. Use Appendix 5 to set environmental codes (water/cleaning, corrosion, mechanical risk), Appendix 4 for cable/volt-drop calcs, Appendix 6 for certification.

## Slide 6: Example: Section 701
Section 701: Locations containing a bath or shower.
This section details many areas of this environment and clearly highlights zones within this area.
Specialised equipment will need to be installed within some zones.
These items of equipment will have to have a specific level of protection against water ingress.
Notes: Part 7, Section 701, pages 242–246

## Slide 7: IP ratings
This type of protection is deemed to have a certain ‘IP’ code/protection attributed to them, which will be covered within this learning outcome.
This is known as the International Protection Marking, created by the Electrotechnical Commission (IEC).

## Slide 8: Zones within a location containing a bath or shower
Notes: This slide and next 2 show these zones.

## Slide 9: Zones within a location containing a bath or shower
Notes: This slide and next 2 show these zones.

## Slide 10: Zones within a location containing a bath or shower

## Slide 11: Some examples of how these codes are used
Lights for Zone 0: If you wish to include ground lights in your shower enclosure, the fitting must have a minimum rating of IPX7 and be completely immersion-proof. Lights for Zone 1: In this zone, a minimum rating of IPX4 is required, but it is generally accepted that IPX5 will be used. Most shower lights are rated at IPX5.
Light Zone 1 is the area above the bath or shower to a height of 2.25m.
An IPX4 will ensure that the fitting is protected against any spray.
If the light uses 230V, it should be protected 30mA RCD (residual current device) to guard the circuit in this zone.
A 30mA RCD must protect all circuits in a bathroom.

## Slide 12: Continued
Lights for Zone 2: You should have a minimum of IPX4 for lights in this zone.
Outside zones: This is any area that falls outside Zones 0, 1 and 2. This area does not require an IP rating as these should not come into contact with water, but would still suggest a minimum IPX4 due to the environment and steam, etc.

## Slide 13: Equipment fitted in a bath or shower room
Equipment fitted in a bath or shower room must comply to the data shown below.
701.512.2 External influences Installed electrical equipment shall have at least the following degrees of protection:
In zone 0: IPX7
In zones 1 and 2: IPX4.
This requirement does not apply to shaver supply units complying with BS EN 61558-2-5 installed in zone 2 and located where direct spray from showers is unlikely.
Electrical equipment exposed to water jets, e.g. for cleaning purposes, shall have a degree of protection of at least IPX5.
Notes: Part 7, Section 701, page 244

## Slide 14: IP codes
Where, during erection, an enclosure or barrier is provided, to afford protection from direct contact, a degree of protection not less than IP2X or IPXXB is required. Also, accessible horizontal top surfaces shall have a degree of protection equivalent to IP4X.
While not every piece of factory-built equipment will automatically have an IP rating, where there's a risk of dust, water, or other intrusions, adhering to IP codes is a crucial step for safety, reliability, and regulatory compliance.
Summary: IP codes determine the degree of protection given by the equipment that is installed against both solids and liquids.

## Slide 15: IP ratings
IP2x Protected against solid objects of 12.5mm diameter or greater
IP4x Protected against solid objects of 1.0mm diameter or greater on horizontal surfaces
IPx5 Protected against jets of water from any direction
IPx7 Protected for temporary immersed enclosure
IPx8 Protected against total submersion; e.g. equipment installed in Zone 0 of a swimming pool
Notes: https://www.iec.ch/ip-ratings

## Slide 16: Appendix 5 of BS7671
Classifications of external influences: This allows the identification of all aspects of external influences under the three main categories of:
environment
utilisation
construction of buildings.
IP ratings have a direct relationship with the classification of external influences listed in Appendix 5 of BS 7671.
Notes: Part 7, Section 701, page 244

## Slide 17: Summary
You should now be able to:
Explain why Part 7 exists and how it adds to Parts 4-6 for higher-risk locations
Identify the BS 7671 Part 7 sections relevant to typical sites
Recognise when the work is beyond non-specialist competence

## Slide 18
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.