## Slide 1
Occupational Specialism: Electrotechnical Engineering
K1.7 Application of the fundamental principles of national standards
PowerPoint 1.7: Isolation and switching

## Slide 2: Introduction
What is the difference between isolation and switching?

## Slide 3: Objectives
By the end of this session, you should be able to:
Recall the different types of devices for isolation and functional switching
Explain the requirements for device selection, securing, marking, location and operation

## Slide 4: 537: Isolation and switching guidance
Table 537.4 of BS 7671: Protective, isolation and switching device selection.
Device | Standard | Isolation | Emergency switching | Functional switching
Switching devices | BS EN 50428 BS EN 60669-1 BS 60947-5-1 | No No No | No No No | Yes Yes Yes
RCD | BS EN 60947-2 BS EN 61009-1 | Yes Yes | Yes Yes | Yes Yes
Isolation switch | BS EN 60669-2-4 | Yes | Yes | Yes
Plug and socket outlet | BS 5733 | Yes | No | Yes

## Slide 5: 537: Isolation and switching
Every installation is to be provided with an effective way to cut off all sources of energy from the supply.
The functions addressed are:
isolation
emergency switching
functional switching
mechanical maintenance.

## Slide 6: 537.2: Devices for isolation
537.2.4 No inadvertent operation allowed.
537.2.5 Provision made for securing isolator.
537.2.7 Identified by position or clear marking as to the installation it isolates.
537.2.8 Links in the neutral, disconnected by tool and accessible to a skilled person only.

## Slide 7
System | Single-phase | Three-phase
Main switch |  | 
TN-S | All live conductors (line and neutral) | Line conductors only (brown, black and grey phases)
TN-C-S |  | 
Other isolators |  | 
TN-S | Line conductors only (brown, black and grey phases) | 
TN-C-S |  | 
All locations |  | 
TT | All live conductors (brown, black and grey phases and neutral) | 

## Slide 8: 537.3.2 – Switching off for mechanical maintenance
What is the difference between an isolator and a switch?
An isolator is an off-load device.
A switch is an on-load device.

## Slide 9: 537.3.2
Mechanical maintenance: The replacement, refurbishment or cleaning of lamps and non-electrical parts of equipment, plant and machinery.
Regulation | Demand
537.3.2.2 | It is preferred to be fitted in the main supply circuit to the equipment.
537.3.2.2 | It must be capable of switching the full load current.
537.3.2.3 | Shall require manual operation.
537.3.2.3 | The open position of the contacts of the device shall be visible or be clearly and reliably indicated.
537.3.2.4 | Must be clearly identified by position or durable marking so as to be identifiable for their intended use.
537.3.2.4 | Identified as to its purposes with an appropriate label. Located at a suitable position.

## Slide 10: 537.3.3: Devices for emergency switching off
Emergency switching off is an emergency operation intended to switch off the supply of electrical energy to all or part of an installation.
537.3.3.2 The devices for emergency switching off shall be capable of breaking the full load current of the relevant parts of the installation.
537.3.3.3 Means for emergency switching off may consist of:
one switching device capable of directly cutting off the appropriate supply, or
a combination of devices activated by a single action for the purpose of cutting off the appropriate supply.
Plugs and socket-outlets shall not be provided for use as a means for emergency switching off.

## Slide 11: 537.3.3
Emergency switching off is an emergency operation intended to switch off the supply of electrical energy to all or part of an installation.
537.3.3.5 The means of operating (handles, push-buttons, etc.) devices for emergency switching off shall be clearly identified, preferably by colour. If a colour is used for identification, this shall be red with a contrasting background (e.g. yellow).
Note: the contrasting background may or may not include text.
537.3.3.7 The means of operation of a device for emergency switching off shall be capable of latching in the 'OFF' position.

## Slide 12: Example of emergency switching control unit
Stop button de-energises all circuits.
Retaining contacts prevent restarting.

## Slide 13: 537.4: Firefighter’s switches
A firefighter’s switch is a device intended for use by the fire service, although not exclusively.
Its purpose is to de-energise designated parts of an installation that operate at a voltage in excess of low voltage (e.g. neon lighting).

## Slide 14
The OFF
position
must be
at the top.
537.4: Firefighter’s switches
The nameplate on the switch near it should be marked with the words: Firefighter’s switch.

## Slide 15
Firefighter’s switch
Minimum size of lettering:
(Regulation: 537.4.4)
10mm high
The OFF position
must be at the TOP
(Regulation: 537.4.4)
The nameplate on the switch
near it should be marked with
the words
‘FIREFIGHTER’S SWITCH’ or
FIRE SWITCH
(Regulation: 537.4.4)
The maximum
height above
the ground is 2.75m
(Regulation: 537.4.2.2[iii])
For an interior installation, where should the firefighter’s switch be situated?
Main entrance to building – 537.4.2.2

## Slide 16: 538: Monitoring devices
Insulation monitoring devices (IMDs) for IT systems (538.1)
An IMD is designed to indicate any important reduction of the insulation level of the system in order to find the cause before a second insulation fault occurs, thus avoiding any power supply interruption.
Residual current monitor (RCM) (538.4)
A residual current monitor permanently monitors any leakage current in the downstream installation or part of it.

## Slide 17: 528: Proximity of wiring systems to other services
528.1 Neither a voltage Band I nor a voltage Band II circuit shall be contained in the same wiring system as a circuit of nominal voltage exceeding that of low voltage and a Band I circuit shall not be contained in the same system as Band II circuit (unless):
every cable or conductor is insulated for the highest voltage present
each conductor of a multicore cable is insulated for the highest voltage present in the cable
the cables are insulated for their system voltage and installed in a separate compartment of a cable ducting or cable trunking system
the cables are installed on a cable tray system where physical separation is provided by a partition
a separate conduit, trunking or ducting system is employed.

## Slide 18: Summary
You should now be able to:
Recall the different types of devices for isolation and functional switching
Explain the requirements for device selection, securing, marking, location and operation

## Slide 19
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.